Table of Contents
Program Version:EnergyPlus, Version 9.1.0-08d2e308bb, YMD=2019.06.19 07:52
Tabular Output Report in Format: HTML
Building: Building
Environment: RUNPERIOD 1 ** TENA - - MN7 WMO#=999
Simulation Timestamp: 2019-06-19 07:53:09

Table of Contents
Report: Annual Building Utility Performance Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Values gathered over 8760.00 hours
Site and Source Energy
	Total Energy [kWh]	Energy Per Total Building Area [kWh/m2]	Energy Per Conditioned Building Area [kWh/m2]
Total Site Energy	113115.59	122.00	122.00
Net Site Energy	101130.63	109.07	109.07
Total Source Energy	253320.32	273.21	273.21
Net Source Energy	215363.95	232.27	232.27

Site to Source Energy Conversion Factors
	Site=>Source Conversion Factor
Electricity	3.167
Natural Gas	1.084
District Cooling	1.056
District Heating	3.613
Steam	0.300
Gasoline	1.050
Diesel	1.050
Coal	1.050
Fuel Oil #1	1.050
Fuel Oil #2	1.050
Propane	1.050
Other Fuel 1	1.000
Other Fuel 2	1.000

Building Area
	Area [m2]
Total Building Area	927.20
Net Conditioned Building Area	927.20
Unconditioned Building Area	0.00

End Uses
	Electricity [kWh]	Natural Gas [kWh]	Additional Fuel [kWh]	District Cooling [kWh]	District Heating [kWh]	Water [m3]
Heating	0.00	6885.66	0.00	0.00	0.00	0.00
Cooling	12487.96	0.00	0.00	0.00	0.00	0.00
Interior Lighting	22566.38	0.00	0.00	0.00	0.00	0.00
Exterior Lighting	0.00	0.00	0.00	0.00	0.00	0.00
Interior Equipment	13249.20	0.00	0.00	0.00	0.00	0.00
Exterior Equipment	0.00	0.00	0.00	0.00	0.00	0.00
Fans	2297.66	0.00	0.00	0.00	0.00	0.00
Pumps	643.31	0.00	0.00	0.00	0.00	0.00
Heat Rejection	0.00	0.00	0.00	0.00	0.00	0.00
Humidification	0.00	0.00	0.00	0.00	0.00	0.00
Heat Recovery	0.00	0.00	0.00	0.00	0.00	0.00
Water Systems	0.00	0.00	0.00	0.00	9473.13	238.79
Refrigeration	0.00	0.00	0.00	0.00	0.00	0.00
Generators	0.00	45512.30	0.00	0.00	0.00	0.00

Total End Uses	51244.50	52397.95	0.00	0.00	9473.13	238.79

Note: Natural gas appears to be the principal heating source based on energy usage.
End Uses By Subcategory
	Subcategory	Electricity [kWh]	Natural Gas [kWh]	Additional Fuel [kWh]	District Cooling [kWh]	District Heating [kWh]	Water [m3]
Heating	Boiler	0.00	6885.66	0.00	0.00	0.00	0.00
	Boiler Parasitic	0.00	0.00	0.00	0.00	0.00	0.00
Cooling	General	12487.96	0.00	0.00	0.00	0.00	0.00
Interior Lighting	GeneralLights	22566.38	0.00	0.00	0.00	0.00	0.00
Exterior Lighting	General	0.00	0.00	0.00	0.00	0.00	0.00
Interior Equipment	General	13249.20	0.00	0.00	0.00	0.00	0.00
Exterior Equipment	General	0.00	0.00	0.00	0.00	0.00	0.00
Fans	General	2297.66	0.00	0.00	0.00	0.00	0.00
Pumps	General	643.31	0.00	0.00	0.00	0.00	0.00
Heat Rejection	General	0.00	0.00	0.00	0.00	0.00	0.00
Humidification	General	0.00	0.00	0.00	0.00	0.00	0.00
Heat Recovery	General	0.00	0.00	0.00	0.00	0.00	0.00
Water Systems	Bathrooms	0.00	0.00	0.00	0.00	4852.09	139.29
	Kitchen Sink	0.00	0.00	0.00	0.00	4621.04	99.50
Refrigeration	General	0.00	0.00	0.00	0.00	0.00	0.00
Generators	General	0.00	45512.30	0.00	0.00	0.00	0.00

Normalized Metrics
Utility Use Per Conditioned Floor Area
	Electricity Intensity [kWh/m2]	Natural Gas Intensity [kWh/m2]	Additional Fuel Intensity [kWh/m2]	District Cooling Intensity [kWh/m2]	District Heating Intensity [kWh/m2]	Water Intensity [m3/m2]
Lighting	24.34	0.00	0.00	0.00	0.00	0.00
HVAC	16.64	7.43	0.00	0.00	10.22	0.26
Other	14.29	49.09	0.00	0.00	0.00	0.00
Total	55.27	56.51	0.00	0.00	10.22	0.26

Utility Use Per Total Floor Area
	Electricity Intensity [kWh/m2]	Natural Gas Intensity [kWh/m2]	Additional Fuel Intensity [kWh/m2]	District Cooling Intensity [kWh/m2]	District Heating Intensity [kWh/m2]	Water Intensity [m3/m2]
Lighting	24.34	0.00	0.00	0.00	0.00	0.00
HVAC	16.64	7.43	0.00	0.00	10.22	0.26
Other	14.29	49.09	0.00	0.00	0.00	0.00
Total	55.27	56.51	0.00	0.00	10.22	0.26

Electric Loads Satisfied
	Electricity [kWh]	Percent Electricity [%]
Fuel-Fired Power Generation	11984.960	23.39
High Temperature Geothermal*	0.000	0.00
Photovoltaic Power	0.000	0.00
Wind Power	0.000	0.00
Power Conversion	0.000	0.00
Net Decrease in On-Site Storage	0.000	0.00
Total On-Site Electric Sources	11984.960	23.39

Electricity Coming From Utility	41464.798	80.92
Surplus Electricity Going To Utility	2205.254	4.30
Net Electricity From Utility	39259.544	76.61

Total On-Site and Utility Electric Sources	51244.504	100.00
Total Electricity End Uses	51244.504	100.00

On-Site Thermal Sources
	Heat [kWh]	Percent Heat [%]
Water-Side Heat Recovery	0.00
Air to Air Heat Recovery for Cooling	0.00
Air to Air Heat Recovery for Heating	0.00
High-Temperature Geothermal*	0.00
Solar Water Thermal	0.00
Solar Air Thermal	0.00
Total On-Site Thermal Sources	0.00

Water Source Summary
	Water [m3]	Percent Water [%]
Rainwater Collection	0.00	0.00
Condensate Collection	0.00	0.00
Groundwater Well	0.00	0.00
Total On Site Water Sources	0.00	0.00
-	-	-
Initial Storage	0.00	0.00
Final Storage	0.00	0.00
Change in Storage	0.00	0.00
-	-	-
Water Supplied by Utility	238.79	100.00
-	-	-
Total On Site, Change in Storage, and Utility Water Sources	238.79	100.00
Total Water End Uses	238.79	100.00

Setpoint Not Met Criteria
	Degrees [deltaC]
Tolerance for Zone Heating Setpoint Not Met Time	0.20
Tolerance for Zone Cooling Setpoint Not Met Time	0.20

Comfort and Setpoint Not Met Summary
	Facility [Hours]
Time Setpoint Not Met During Occupied Heating	0.00
Time Setpoint Not Met During Occupied Cooling	273.00
Time Not Comfortable Based on Simple ASHRAE 55-2004	1246.75

Note 1: An asterisk (*) indicates that the feature is not yet implemented.

Table of Contents
Top
Annual Building Utility Performance Summary
Input Verification and Results Summary
Demand End Use Components Summary
Source Energy End Use Components Summary
Component Sizing Summary
Surface Shadowing Summary
Adaptive Comfort Summary
Initialization Summary
Annual Heat Emissions Summary
Climatic Data Summary
Envelope Summary
Shading Summary
Lighting Summary
Equipment Summary
HVAC Sizing Summary
Coil Sizing Details
System Summary
Outdoor Air Summary
Object Count Summary
Energy Meters
Sensible Heat Gain Summary
Standard 62.1 Summary
LEED Summary
ZONE COOLING SUMMARY
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
ZONE HEATING SUMMARY
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
ZONE ELECTRIC SUMMARY
| SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
SPACE GAINS
| SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
PEAK SPACE GAINS
| SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
SPACE GAIN COMPONENTS AT COOLING PEAK
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
ENERGY CONSUMPTION - ELECTRICITY & NATURAL GAS
| Meter |
ENERGY CONSUMPTION - ELECTRICITY GENERATED & PROPANE
| Meter |
ENERGY CONSUMPTION - PURCHASED HEATING & COOLING
| Meter |
END-USE ENERGY CONSUMPTION - ELECTRICITY
| Meter |
END-USE ENERGY CONSUMPTION - NATURAL GAS
| Meter |
PEAK ENERGY END-USE - ELECTRICITY PART 1
| Meter |
PEAK ENERGY END-USE - ELECTRICITY PART 2
| Meter |
ELECTRIC COMPONENTS OF PEAK DEMAND
| Meter |
PEAK ENERGY END-USE - NATURAL GAS
| Meter |
SETPOINTS NOT MET WITH TEMPERATURES
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
COMFORT REPORT - SIMPLE 55
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
OCCUPANT COMFORT DATA SUMMARY
| SPACE1-1 PEOPLE 1 | SPACE2-1 PEOPLE 1 | SPACE3-1 PEOPLE 1 | SPACE4-1 PEOPLE 1 | SPACE5-1 PEOPLE 1 |
CHILLER REPORT
| CENTRAL CHILLER |
BOILER REPORT
| CENTRAL BOILER |
DX REPORT
| MAIN COOLING COIL 1 |
WINDOW REPORT
| WF-1 | DF-1 | WR-1 | WB-1 | DB-1 | WL-1 |
WINDOW ENERGY REPORT
| WF-1 | DF-1 | WR-1 | WB-1 | DB-1 | WL-1 |
WINDOW ZONE SUMMARY
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
WINDOW ENERGY ZONE SUMMARY
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
AVERAGE OUTDOOR CONDITIONS
| Environment |
OUTDOOR CONDITIONS MAXIMUM DRYBULB
| Environment |
OUTDOOR CONDITIONS MINIMUM DRYBULB
| Environment |
OUTDOOR CONDITIONS MAXIMUM WETBULB
| Environment |
OUTDOOR CONDITIONS MAXIMUM DEW POINT
| Environment |
OUTDOOR GROUND CONDITIONS
| Environment |
GENERATOR REPORT
| SMALLMICROTURBINE |
DAYLIGHTING REPORT
| Environment |
COIL REPORT
| SPACE1-1 ZONE COIL | SPACE2-1 ZONE COIL | SPACE3-1 ZONE COIL | SPACE4-1 ZONE COIL | SPACE5-1 ZONE COIL | MAIN HEATING COIL 1 | MAIN COOLING COIL 1 |
PLANT LOOP DEMAND REPORT
| HOT WATER LOOP | CHILLED WATER LOOP |
FAN REPORT
| SUPPLY FAN 1 |
PUMP REPORT
| HW CIRC PUMP | CW CIRC PUMP |
COND LOOP DEMAND REPORT
| HOT WATER LOOP | CHILLED WATER LOOP |
ZONE TEMPERATURE OSCILLATION REPORT
| PLENUM-1 | SPACE1-1 | SPACE2-1 | SPACE3-1 | SPACE4-1 | SPACE5-1 |
Tariff Report
| WATER TARIFF | EXAMPLEA | EXAMPLEA-GAS | EXAMPLEAWITHVARIABLEMONTHLYCHARGE | EXAMPLEB | EXAMPLEC | EXAMPLED | EXAMPLEDWITHRATCHET | EXAMPLEE | EXAMPLEF | EXAMPLEFMC | EXAMPLEG | EXAMPLEH | EXAMPLEI-SELL | EXAMPLEI-NETMETER |
Economics Results Summary Report
| Entire Facility |
Life-Cycle Cost Report
| Entire Facility |

Table of Contents
Report: Input Verification and Results Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
General
	Value
Program Version and Build	EnergyPlus, Version 9.1.0-08d2e308bb, YMD=2019.06.19 07:52
RunPeriod	RUNPERIOD 1
Weather File	TENA - - MN7 WMO#=999
Latitude [deg]	-1.0
Longitude [deg]	-77.8
Elevation [m]	499.00
Time Zone	-5.0
North Axis Angle [deg]	30.00
Rotation for Appendix G [deg]	0.00
Hours Simulated [hrs]	8760.00

ENVELOPE
Window-Wall Ratio
	Total	North (315 to 45 deg)	East (45 to 135 deg)	South (135 to 225 deg)	West (225 to 315 deg)
Gross Wall Area [m2]	274.20	91.50	45.60	91.50	45.60
Above Ground Wall Area [m2]	274.20	91.50	45.60	91.50	45.60
Window Opening Area [m2]	60.90	20.85	9.12	21.81	9.12
Gross Window-Wall Ratio [%]	22.21	22.79	20.00	23.84	20.00
Above Ground Window-Wall Ratio [%]	22.21	22.79	20.00	23.84	20.00

Conditioned Window-Wall Ratio
	Total	North (315 to 45 deg)	East (45 to 135 deg)	South (135 to 225 deg)	West (225 to 315 deg)
Gross Wall Area [m2]	274.20	91.50	45.60	91.50	45.60
Above Ground Wall Area [m2]	274.20	91.50	45.60	91.50	45.60
Window Opening Area [m2]	60.90	20.85	9.12	21.81	9.12
Gross Window-Wall Ratio [%]	22.21	22.79	20.00	23.84	20.00
Above Ground Window-Wall Ratio [%]	22.21	22.79	20.00	23.84	20.00

Skylight-Roof Ratio
	Total
Gross Roof Area [m2]	463.60
Skylight Area [m2]	0.00
Skylight-Roof Ratio [%]	0.00

PERFORMANCE
Zone Summary
	Area [m2]	Conditioned (Y/N)	Part of Total Floor Area (Y/N)	Volume [m3]	Multipliers	Above Ground Gross Wall Area [m2]	Underground Gross Wall Area [m2]	Window Glass Area [m2]	Opening Area [m2]	Lighting [W/m2]	People [m2 per person]	Plug and Process [W/m2]
PLENUM-1	463.60	Yes	Yes	283.20	1.00	54.84	0.00	0.00	0.00	0.0000		0.0000
SPACE1-1	99.16	Yes	Yes	239.25	1.00	73.20	0.00	21.81	21.81	15.9742	9.01	10.6495
SPACE2-1	42.73	Yes	Yes	103.31	1.00	36.48	0.00	9.12	9.12	16.0056	8.55	10.6704
SPACE3-1	96.48	Yes	Yes	239.25	1.00	73.20	0.00	20.85	20.85	16.4179	8.77	10.9453
SPACE4-1	42.73	Yes	Yes	103.31	1.00	36.48	0.00	9.12	9.12	16.0056	8.55	10.6704
SPACE5-1	182.49	Yes	Yes	447.68	1.00	0.00	0.00	0.00	0.00	16.2420	9.12	10.8280
Total	927.20			1416.00		274.20	0.00	60.90	60.90	8.0889	17.83	5.3926
Conditioned Total	927.20			1416.00		274.20	0.00	60.90	60.90	8.0889	17.83	5.3926
Unconditioned Total	0.00			0.00		0.00	0.00	0.00	0.00
Not Part of Total	0.00			0.00		0.00	0.00	0.00	0.00

Table of Contents
Report: Demand End Use Components Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
End Uses
	Electricity [W]	Natural Gas [W]	Propane [W]	District Cooling [W]	District Heating [W]	Water [m3/s]
Time of Peak	22-MAR-10:00	12-SEP-06:15	-	-	01-JAN-12:15	01-JAN-12:15
Heating	0.00	25979.51	0.00	0.00	0.00	0.00
Cooling	7086.84	0.00	0.00	0.00	0.00	0.00
Interior Lighting	7500.00	0.00	0.00	0.00	0.00	0.00
Exterior Lighting	0.00	0.00	0.00	0.00	0.00	0.00
Interior Equipment	4500.00	0.00	0.00	0.00	0.00	0.00
Exterior Equipment	0.00	0.00	0.00	0.00	0.00	0.00
Fans	853.80	0.00	0.00	0.00	0.00	0.00
Pumps	172.04	0.00	0.00	0.00	0.00	0.00
Heat Rejection	0.00	0.00	0.00	0.00	0.00	0.00
Humidification	0.00	0.00	0.00	0.00	0.00	0.00
Heat Recovery	0.00	0.00	0.00	0.00	0.00	0.00
Water Systems	0.00	0.00	0.00	0.00	4747.65	0.00
Refrigeration	0.00	0.00	0.00	0.00	0.00	0.00
Generators	0.00	5464.47	0.00	0.00	0.00	0.00

Total End Uses	20112.67	31443.99	0.00	0.00	4747.65	0.00

End Uses By Subcategory
	Subcategory	Electricity [W]	Natural Gas [W]	Propane [W]	District Cooling [W]	District Heating [W]	Water [m3/s]
Heating	Boiler	0.00	25979.51	0.00	0.00	0.00	0.00
	Boiler Parasitic	0.00	0.00	0.00	0.00	0.00	0.00
Cooling	General	7086.84	0.00	0.00	0.00	0.00	0.00
Interior Lighting	GeneralLights	7500.00	0.00	0.00	0.00	0.00	0.00
Exterior Lighting	General	0.00	0.00	0.00	0.00	0.00	0.00
Interior Equipment	General	4500.00	0.00	0.00	0.00	0.00	0.00
Exterior Equipment	General	0.00	0.00	0.00	0.00	0.00	0.00
Fans	General	853.80	0.00	0.00	0.00	0.00	0.00
Pumps	General	172.04	0.00	0.00	0.00	0.00	0.00
Heat Rejection	General	0.00	0.00	0.00	0.00	0.00	0.00
Humidification	General	0.00	0.00	0.00	0.00	0.00	0.00
Heat Recovery	General	0.00	0.00	0.00	0.00	0.00	0.00
Water Systems	Bathrooms	0.00	0.00	0.00	0.00	1582.55	0.00
	Kitchen Sink	0.00	0.00	0.00	0.00	3165.10	0.00
Refrigeration	General	0.00	0.00	0.00	0.00	0.00	0.00
Generators	General	0.00	5464.47	0.00	0.00	0.00	0.00

Table of Contents
Report: Source Energy End Use Components Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Values gathered over 8760.00 hours
Source Energy End Use Components Summary
	Source Electricity [kWh]	Source Natural Gas [kWh]	Source Additional Fuel [kWh]	Source District Cooling [kWh]	Source District Heating [kWh]
Heating	0.00	7464.05	0.00	0.00	0.00
Cooling	39549.37	0.00	0.00	0.00	0.00
Interior Lighting	71467.71	0.00	0.00	0.00	0.00
Exterior Lighting	0.00	0.00	0.00	0.00	0.00
Interior Equipment	41960.22	0.00	0.00	0.00	0.00
Exterior Equipment	0.00	0.00	0.00	0.00	0.00
Fans	7276.68	0.00	0.00	0.00	0.00
Pumps	2037.37	0.00	0.00	0.00	0.00
Heat Rejection	0.00	0.00	0.00	0.00	0.00
Humidification	0.00	0.00	0.00	0.00	0.00
Heat Recovery	0.00	0.00	0.00	0.00	0.00
Water Systems	0.00	0.00	0.00	0.00	34229.59
Refrigeration	0.00	0.00	0.00	0.00	0.00
Generators	0.00	49335.33	0.00	0.00	0.00

Total Source Energy End Use Components	162291.34	56799.38	0.00	0.00	34229.59

Normalized Metrics
Source Energy End Use Components Per Conditioned Floor Area
	Source Electricity [kWh/m2]	Source Natural Gas [kWh/m2]	Source Additional Fuel [kWh/m2]	Source District Cooling [kWh/m2]	Source District Heating [kWh/m2]
Heating	0.00	8.05	0.00	0.00	0.00
Cooling	42.65	0.00	0.00	0.00	0.00
Interior Lighting	77.08	0.00	0.00	0.00	0.00
Exterior Lighting	0.00	0.00	0.00	0.00	0.00
Interior Equipment	45.25	0.00	0.00	0.00	0.00
Exterior Equipment	0.00	0.00	0.00	0.00	0.00
Fans	7.85	0.00	0.00	0.00	0.00
Pumps	2.20	0.00	0.00	0.00	0.00
Heat Rejection	0.00	0.00	0.00	0.00	0.00
Humidification	0.00	0.00	0.00	0.00	0.00
Heat Recovery	0.00	0.00	0.00	0.00	0.00
Water Systems	0.00	0.00	0.00	0.00	36.92
Refrigeration	0.00	0.00	0.00	0.00	0.00
Generators	0.00	53.21	0.00	0.00	0.00

Total Source Energy End Use Components	175.03	61.26	0.00	0.00	36.92

Source Energy End Use Components Per Total Floor Area
	Source Electricity [kWh/m2]	Source Natural Gas [kWh/m2]	Source Additional Fuel [kWh/m2]	Source District Cooling [kWh/m2]	Source District Heating [kWh/m2]
Heating	0.00	8.05	0.00	0.00	0.00
Cooling	42.65	0.00	0.00	0.00	0.00
Interior Lighting	77.08	0.00	0.00	0.00	0.00
Exterior Lighting	0.00	0.00	0.00	0.00	0.00
Interior Equipment	45.25	0.00	0.00	0.00	0.00
Exterior Equipment	0.00	0.00	0.00	0.00	0.00
Fans	7.85	0.00	0.00	0.00	0.00
Pumps	2.20	0.00	0.00	0.00	0.00
Heat Rejection	0.00	0.00	0.00	0.00	0.00
Humidification	0.00	0.00	0.00	0.00	0.00
Heat Recovery	0.00	0.00	0.00	0.00	0.00
Water Systems	0.00	0.00	0.00	0.00	36.92
Refrigeration	0.00	0.00	0.00	0.00	0.00
Generators	0.00	53.21	0.00	0.00	0.00

Total Source Energy End Use Components	175.03	61.26	0.00	0.00	36.92

Table of Contents
Report: Component Sizing Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
AirTerminal:SingleDuct:VAV:Reheat
	Design Size Maximum Air Flow Rate [m3/s]	Design Size Constant Minimum Air Flow Fraction	User-Specified Constant Minimum Air Flow Fraction	Design Size Minimum Air Flow Rate [m3/s]	Design Size Maximum Flow Fraction during Reheat []	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	Design Size Maximum Reheat Water Flow Rate [m3/s]	Design Size Reheat Coil Sizing Air Volume Flow Rate [m3/s]	Design Size Reheat Coil Sizing Inlet Air Temperature [C]	Design Size Reheat Coil Sizing Inlet Air Humidity Ratio [kgWater/kgDryAir]
SPACE1-1 VAV REHEAT	0.265197	0.284920	0.400000	0.106079	0.759786	0.002032	0.000133	0.157166	16.70	0.008000
SPACE2-1 VAV REHEAT	0.151020	0.215627	0.400000	0.060408	0.937466	0.003313	0.000056	0.066158	16.70	0.008000
SPACE3-1 VAV REHEAT	0.522318	0.200000	0.400000	0.208927	0.400000	0.002165	0.000137	0.208927	16.70	0.008000
SPACE4-1 VAV REHEAT	0.311786	0.200000	0.400000	0.124714	0.454081	0.003313	0.000064	0.124714	16.70	0.008000
SPACE5-1 VAV REHEAT	0.295176	0.471101	0.400000	0.118070	1.00	0.001617	0.000103	0.121375	16.70	0.008000

User-Specified values were used. Design Size values were used if no User-Specified values were provided. Design Size values may be derived from alternate User-Specified values.
Coil:Heating:Water
	Design Size Rated Capacity [W]	Design Size Maximum Water Flow Rate [m3/s]	Design Size U-Factor Times Area Value [W/K]
SPACE1-1 ZONE COIL	6011.33	0.000133	147.22
SPACE2-1 ZONE COIL	2530.40	0.000056	61.97
SPACE3-1 ZONE COIL	6198.12	0.000137	137.95
SPACE4-1 ZONE COIL	2900.13	0.000064	60.80
SPACE5-1 ZONE COIL	4641.97	0.000103	113.68
MAIN HEATING COIL 1	17975.12	0.000397	241.47

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
AirLoopHVAC
	Sum of Air Terminal Maximum Heating Flow Rates [m3/s]	Sum of Air Terminal Minimum Heating Flow Rates [m3/s]	Sum of Air Terminal Maximum Flow Rates [m3/s]	Adjusted Heating Design Air Flow Rate [m3/s]	Adjusted Cooling Design Air Flow Rate [m3/s]	Adjusted Main Design Air Flow Rate [m3/s]	User Heating Air Flow Ratio []	Calculated Heating Air Flow Ratio []	Design Supply Air Flow Rate [m3/s]
VAV SYS 1	0.988748	0.618199	1.55	0.988748	1.55	1.55	0.300000	0.639761	1.55

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Controller:OutdoorAir
	Maximum Outdoor Air Flow Rate [m3/s]	Minimum Outdoor Air Flow Rate [m3/s]
OA CONTROLLER 1	1.55	0.490880

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Coil:Cooling:Water
	Design Size Design Inlet Air Temperature [C]	Design Size Design Inlet Water Temperature [C]	Design Size Design Outlet Air Temperature [C]	Design Size Design Inlet Air Humidity Ratio	Design Size Design Outlet Air Humidity Ratio	Design Size Design Coil Load [W]	Design Size Design Water Flow Rate [m3/s]	Design Size Design Air Flow Rate [m3/s]
MAIN COOLING COIL 1	26.53	7.22	12.06	0.011256	0.008000	40439.26	0.001444	1.55

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Fan:VariableVolume
	Design Size Maximum Flow Rate [m3/s]
SUPPLY FAN 1	1.55

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Controller:WaterCoil
	Maximum Actuated Flow [m3/s]
CENTRAL COOLING COIL CONTOLLER 1	0.001444
CENTRAL HEATING COIL CONTOLLER 1	0.000397

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
PlantLoop
	Maximum Loop Flow Rate [m3/s]	Plant Loop Volume [m3]
HOT WATER LOOP	0.000889	0.106732
CHILLED WATER LOOP	0.001444	0.173328

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Pump:VariableSpeed
	Design Flow Rate [m3/s]	Design Power Consumption [W]
HW CIRC PUMP	0.000889	227.24
CW CIRC PUMP	0.001444	369.02

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Boiler:HotWater
	Design Size Nominal Capacity [W]	Design Size Design Water Flow Rate [m3/s]
CENTRAL BOILER	40257.07	0.000889

User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Chiller:Electric
	Design Size Nominal Capacity [W]	Design Size Design Chilled Water Flow Rate [m3/s]	User-Specified Design Condenser Water Flow Rate [m3/s]
CENTRAL CHILLER	40439.26	0.001444	0.001100

User-Specified values were used. Design Size values were used if no User-Specified values were provided.

Table of Contents
Report: Surface Shadowing Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Surfaces (Walls, Roofs, etc) that may be Shadowed by Other Surfaces
	Possible Shadow Receivers
MAIN SOUTH OVERHANG	FRONT-1 |
Mir-MAIN SOUTH OVERHANG	SOUTH DOOR OVERHANG | WALL-1PF | FRONT-1 |
SOUTH DOOR OVERHANG	WALL-1PF |
Mir-SOUTH DOOR OVERHANG	WALL-1PF |
WALL-1PF	SOUTH DOOR OVERHANG |
FRONT-1	MAIN SOUTH OVERHANG | SOUTH DOOR OVERHANG |

Subsurfaces (Windows and Doors) that may be Shadowed by Surfaces
	Possible Shadow Receivers
FRONT-1	WF-1 | DF-1 |
RIGHT-1	WR-1 |
BACK-1	WB-1 | DB-1 |
LEFT-1	WL-1 |

Table of Contents
Report: Adaptive Comfort Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Time Not Meeting the Adaptive Comfort Models during Occupied Hours
ASHRAE55 90% Acceptability Limits [Hours]	ASHRAE55 80% Acceptability Limits [Hours]	CEN15251 Category I Acceptability Limits [Hours]	CEN15251 Category II Acceptability Limits [Hours]	CEN15251 Category III Acceptability Limits [Hours]

Table of Contents
Report: Initialization Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Version
	Version ID
1	9.1

Timesteps per Hour
	#TimeSteps	Minutes per TimeStep {minutes}
1	4	15

System Convergence Limits
	Minimum System TimeStep {minutes}	Max HVAC Iterations	Minimum Plant Iterations	Maximum Plant Iterations
1	1	20	2	8

Simulation Control
	Do Zone Sizing	Do System Sizing	Do Plant Sizing	Do Design Days	Do Weather Simulation	Do HVAC Sizing Simulation
1	Yes	Yes	Yes	No	Yes	No

Output Reporting Tolerances
	Tolerance for Time Heating Setpoint Not Met	Tolerance for Zone Cooling Setpoint Not Met Time
1	0.200	0.200

Site:GroundTemperature:BuildingSurface
	Jan{C}	Feb{C}	Mar{C}	Apr{C}	May{C}	Jun{C}	Jul{C}	Aug{C}	Sep{C}	Oct{C}	Nov{C}	Dec{C}
1	20.03	20.03	20.13	20.30	20.43	20.52	20.62	20.77	20.78	20.55	20.44	20.20

Site:GroundTemperature:FCfactorMethod
	Jan{C}	Feb{C}	Mar{C}	Apr{C}	May{C}	Jun{C}	Jul{C}	Aug{C}	Sep{C}	Oct{C}	Nov{C}	Dec{C}
1	23.60	23.80	23.90	23.80	23.60	23.20	22.90	22.70	22.60	22.70	22.90	23.20

Site:GroundTemperature:Shallow
	Jan{C}	Feb{C}	Mar{C}	Apr{C}	May{C}	Jun{C}	Jul{C}	Aug{C}	Sep{C}	Oct{C}	Nov{C}	Dec{C}
1	13.00	13.00	13.00	13.00	13.00	13.00	13.00	13.00	13.00	13.00	13.00	13.00

Site:GroundTemperature:Deep
	Jan{C}	Feb{C}	Mar{C}	Apr{C}	May{C}	Jun{C}	Jul{C}	Aug{C}	Sep{C}	Oct{C}	Nov{C}	Dec{C}
1	16.00	16.00	16.00	16.00	16.00	16.00	16.00	16.00	16.00	16.00	16.00	16.00

Site:GroundReflectance
	Jan{dimensionless}	Feb{dimensionless}	Mar{dimensionless}	Apr{dimensionless}	May{dimensionless}	Jun{dimensionless}	Jul{dimensionless}	Aug{dimensionless}	Sep{dimensionless}	Oct{dimensionless}	Nov{dimensionless}	Dec{dimensionless}
1	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20

Site:GroundReflectance:SnowModifier
	Normal	Daylighting {dimensionless}
1	1.000	1.000

Site:GroundReflectance:Snow
	Jan{dimensionless}	Feb{dimensionless}	Mar{dimensionless}	Apr{dimensionless}	May{dimensionless}	Jun{dimensionless}	Jul{dimensionless}	Aug{dimensionless}	Sep{dimensionless}	Oct{dimensionless}	Nov{dimensionless}	Dec{dimensionless}
1	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20

Site:GroundReflectance:Snow:Daylighting
	Jan{dimensionless}	Feb{dimensionless}	Mar{dimensionless}	Apr{dimensionless}	May{dimensionless}	Jun{dimensionless}	Jul{dimensionless}	Aug{dimensionless}	Sep{dimensionless}	Oct{dimensionless}	Nov{dimensionless}	Dec{dimensionless}
1	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20	0.20

Environment:Weather Station
	Wind Sensor Height Above Ground {m}	Wind Speed Profile Exponent {}	Wind Speed Profile Boundary Layer Thickness {m}	Air Temperature Sensor Height Above Ground {m}	Wind Speed Modifier Coefficient-Internal	Temperature Modifier Coefficient-Internal
1	10.000	0.140	270.000	1.500	1.586	9.750E-003

Site:Location
	Location Name	Latitude {N+/S- Deg}	Longitude {E+/W- Deg}	Time Zone Number {GMT+/-}	Elevation {m}	Standard Pressure at Elevation {Pa}	Standard RhoAir at Elevation
1	TENA - - MN7 WMO#=999	-0.98	-77.81	-5.00	499.00	95472	1.1347

Site Water Mains Temperature Information
	Calculation Method{}	Water Mains Temperature Schedule Name{}	Annual Average Outdoor Air Temperature{C}	Maximum Difference In Monthly Average Outdoor Air Temperatures{deltaC}	Fixed Default Water Mains Temperature{C}
1	FixedDefault	NA	NA	NA	10.0

Building Information
	Building Name	North Axis {deg}	Terrain	Loads Convergence Tolerance Value	Temperature Convergence Tolerance Value	Solar Distribution	Maximum Number of Warmup Days	Minimum Number of Warmup Days
1	Building	30.000	City	4.00000E-002	0.40000	FullExterior	25	6

Inside Convection Algorithm
	Algorithm {Simple TARP CeilingDiffuser AdaptiveConvectionAlgorithm}
1	Simple

Outside Convection Algorithm
	Algorithm {SimpleCombined TARP MoWitt DOE-2 AdaptiveConvectionAlgorithm}
1	SimpleCombined

Sky Radiance Distribution
	Value {Anisotropic}
1	Anisotropic

Zone Air Solution Algorithm
	Value {ThirdOrderBackwardDifference AnalyticalSolution EulerMethod}
1	ThirdOrderBackwardDifference

Zone Air Carbon Dioxide Balance Simulation
	Simulation {Yes/No}	Carbon Dioxide Concentration
1	No	N/A

Zone Air Generic Contaminant Balance Simulation
	Simulation {Yes/No}	Generic Contaminant Concentration
1	No	N/A

Zone Air Mass Flow Balance Simulation
	Enforce Mass Balance	Adjust Zone Mixing	Adjust Zone Infiltration {AddInfiltration AdjustInfiltration None}	Infiltration Zones {MixingSourceZonesOnly AllZones}
1	No	N/A	N/A	N/A

HVACSystemRootFindingAlgorithm
	Value {RegulaFalsi Bisection BisectionThenRegulaFalsi RegulaFalsiThenBisection}
1	RegulaFalsi

Environment:Site Atmospheric Variation
	Wind Speed Profile Exponent {}	Wind Speed Profile Boundary Layer Thickness {m}	Air Temperature Gradient Coefficient {K/m}
1	0.330	460.000	6.500000E-003

Surface Geometry
	Starting Corner	Vertex Input Direction	Coordinate System	Daylight Reference Point Coordinate System	Rectangular (Simple) Surface Coordinate System
1	UpperLeftCorner	Counterclockwise	RelativeCoordinateSystem	RelativeCoordinateSystem	RelativeToZoneOrigin

Surface Heat Transfer Algorithm
	Value {CTF - ConductionTransferFunction EMPD - MoisturePenetrationDepthConductionTransferFunction CondFD - ConductionFiniteDifference HAMT - CombinedHeatAndMoistureFiniteElement} - Description	Inside Surface Max Temperature Limit{C}	Surface Convection Coefficient Lower Limit {W/m2-K}	Surface Convection Coefficient Upper Limit {W/m2-K}
1	CTF - ConductionTransferFunction	200	0.10	1000.0

Shading Summary
	Number of Fixed Detached Shades	Number of Building Detached Shades	Number of Attached Shades
1	0	0	4

Zone Summary
	Number of Zones	Number of Zone Surfaces	Number of SubSurfaces
1	6	46	6

Zone Information
	Zone Name	North Axis {deg}	Origin X-Coordinate {m}	Origin Y-Coordinate {m}	Origin Z-Coordinate {m}	Centroid X-Coordinate {m}	Centroid Y-Coordinate {m}	Centroid Z-Coordinate {m}	Type	Zone Multiplier	Zone List Multiplier	Minimum X {m}	Maximum X {m}	Minimum Y {m}	Maximum Y {m}	Minimum Z {m}	Maximum Z {m}	Ceiling Height {m}	Volume {m3}	Zone Inside Convection Algorithm {Simple-Detailed-CeilingDiffuser-TrombeWall}	Zone Outside Convection Algorithm {Simple-Detailed-Tarp-MoWitt-DOE-2-BLAST}	Floor Area {m2}	Exterior Gross Wall Area {m2}	Exterior Net Wall Area {m2}	Exterior Window Area {m2}	Number of Surfaces	Number of SubSurfaces	Number of Shading SubSurfaces	Part of Total Building Area
1	PLENUM-1	0.0	0.00	0.00	0.00	17.01	-1.04	2.70	1	1	1	0.00	34.01	-15.25	13.16	2.40	3.00	0.61	283.20	Simple	Simple	463.60	54.84	54.84	0.00	10	0	0	Yes
2	SPACE1-1	0.0	0.00	0.00	0.00	14.06	-6.15	1.20	1	1	1	0.00	26.41	-15.25	1.35	0.00	2.40	2.44	239.25	Simple	Simple	99.16	73.20	51.39	21.81	6	2	4	Yes
3	SPACE2-1	0.0	0.00	0.00	0.00	28.88	-7.88	1.20	1	1	1	25.06	34.01	-15.25	-2.09	0.00	2.40	2.44	103.31	Simple	Simple	42.74	36.48	27.36	9.12	6	1	0	Yes
4	SPACE3-1	0.0	0.00	0.00	0.00	19.98	4.10	1.20	1	1	1	7.60	34.01	-3.35	13.16	0.00	2.40	2.44	239.25	Simple	Simple	96.48	73.20	52.35	20.85	6	2	0	Yes
5	SPACE4-1	0.0	0.00	0.00	0.00	5.15	5.82	1.20	1	1	1	0.00	9.00	0.00	13.16	0.00	2.40	2.44	103.31	Simple	Simple	42.74	36.48	27.36	9.12	6	1	0	Yes
6	SPACE5-1	0.0	0.00	0.00	0.00	17.03	-1.00	1.20	1	1	1	5.05	29.01	-10.20	8.20	0.00	2.40	2.44	447.68	Simple	Simple	182.49	0.00	0.00	0.00	6	0	0	Yes

Zone Internal Gains Nominal
	Zone Name	Floor Area {m2}	# Occupants	Area per Occupant {m2/person}	Occupant per Area {person/m2}	Interior Lighting {W/m2}	Electric Load {W/m2}	Gas Load {W/m2}	Other Load {W/m2}	Hot Water Eq {W/m2}	Steam Equipment {W/m2}	Sum Loads per Area {W/m2}	Outdoor Controlled Baseboard Heat
1	PLENUM-1	463.60	0.0	N/A	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000	No
2	SPACE1-1	99.16	11.0	9.015	0.111	15.974	10.649	0.000	0.000	0.000	0.000	26.624	No
3	SPACE2-1	42.74	5.0	8.547	0.117	16.006	10.670	0.000	0.000	0.000	0.000	26.676	No
4	SPACE3-1	96.48	11.0	8.771	0.114	16.418	10.945	0.000	0.000	0.000	0.000	27.363	No
5	SPACE4-1	42.74	5.0	8.547	0.117	16.006	10.670	0.000	0.000	0.000	0.000	26.676	No
6	SPACE5-1	182.49	20.0	9.125	0.110	16.242	10.828	0.000	0.000	0.000	0.000	27.070	No

People Internal Gains Nominal
	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Number of People {}	People/Floor Area {person/m2}	Floor Area per person {m2/person}	Fraction Radiant	Fraction Convected	Sensible Fraction Calculation	Activity level	ASHRAE 55 Warnings	Carbon Dioxide Generation Rate	Nominal Minimum Number of People	Nominal Maximum Number of People
1	SPACE1-1 PEOPLE 1	OCCUPY-1	SPACE1-1	99.16	11.0	11.0	0.111	9.015	0.300	0.700	AutoCalculate	ACTSCHD	No	3.8200E-008	0	11
2	SPACE2-1 PEOPLE 1	OCCUPY-1	SPACE2-1	42.74	5.0	5.0	0.117	8.547	0.300	0.700	AutoCalculate	ACTSCHD	No	3.8200E-008	0	5
3	SPACE3-1 PEOPLE 1	OCCUPY-1	SPACE3-1	96.48	11.0	11.0	0.114	8.771	0.300	0.700	AutoCalculate	ACTSCHD	No	3.8200E-008	0	11
4	SPACE4-1 PEOPLE 1	OCCUPY-1	SPACE4-1	42.74	5.0	5.0	0.117	8.547	0.300	0.700	AutoCalculate	ACTSCHD	No	3.8200E-008	0	5
5	SPACE5-1 PEOPLE 1	OCCUPY-1	SPACE5-1	182.49	20.0	20.0	0.110	9.125	0.300	0.700	AutoCalculate	ACTSCHD	No	3.8200E-008	0	20

Lights Internal Gains Nominal
	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Lighting Level {W}	Lights/Floor Area {W/m2}	Lights per person {W/person}	Fraction Return Air	Fraction Radiant	Fraction Short Wave	Fraction Convected	Fraction Replaceable	End-Use Category	Nominal Minimum Lighting Level {W}	Nominal Maximum Lighting Level {W}
1	SPACE1-1 LIGHTS 1	LIGHTS-1	SPACE1-1	99.16	11.0	1584.000	15.974	144.000	0.200	0.590	0.200	1.000E-002	0.000	GeneralLights	79.200	1584.000
2	SPACE2-1 LIGHTS 1	LIGHTS-1	SPACE2-1	42.74	5.0	684.000	16.006	136.800	0.200	0.590	0.200	1.000E-002	0.000	GeneralLights	34.200	684.000
3	SPACE3-1 LIGHTS 1	LIGHTS-1	SPACE3-1	96.48	11.0	1584.000	16.418	144.000	0.200	0.590	0.200	1.000E-002	0.000	GeneralLights	79.200	1584.000
4	SPACE4-1 LIGHTS 1	LIGHTS-1	SPACE4-1	42.74	5.0	684.000	16.006	136.800	0.200	0.590	0.200	1.000E-002	0.000	GeneralLights	34.200	684.000
5	SPACE5-1 LIGHTS 1	LIGHTS-1	SPACE5-1	182.49	20.0	2964.000	16.242	148.200	0.200	0.590	0.200	1.000E-002	0.000	GeneralLights	148.200	2964.000

ElectricEquipment Internal Gains Nominal
	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Equipment Level {W}	Equipment/Floor Area {W/m2}	Equipment per person {W/person}	Fraction Latent	Fraction Radiant	Fraction Lost	Fraction Convected	End-Use SubCategory	Nominal Minimum Equipment Level {W}	Nominal Maximum Equipment Level {W}
1	SPACE1-1 ELECEQ 1	EQUIP-1	SPACE1-1	99.16	11.0	1056.000	10.649	96.000	0.000	0.300	0.000	0.700	General	21.120	950.400
2	SPACE2-1 ELECEQ 1	EQUIP-1	SPACE2-1	42.74	5.0	456.000	10.670	91.200	0.000	0.300	0.000	0.700	General	9.120	410.400
3	SPACE3-1 ELECEQ 1	EQUIP-1	SPACE3-1	96.48	11.0	1056.000	10.945	96.000	0.000	0.300	0.000	0.700	General	21.120	950.400
4	SPACE4-1 ELECEQ 1	EQUIP-1	SPACE4-1	42.74	5.0	456.000	10.670	91.200	0.000	0.300	0.000	0.700	General	9.120	410.400
5	SPACE5-1 ELECEQ 1	EQUIP-1	SPACE5-1	182.49	20.0	1976.000	10.828	98.800	0.000	0.300	0.000	0.700	General	39.520	1778.400

Shadowing/Sun Position Calculations Annual Simulations
	Calculation Method	Value {days}	Allowable Number Figures in Shadow Overlap {}	Polygon Clipping Algorithm	Sky Diffuse Modeling Algorithm	External Shading Calculation Method	Output External Shading Calculation Results	Disable Self-Shading Within Shading Zone Groups	Disable Self-Shading From Shading Zone Groups to Other Zones
1	AverageOverDaysInFrequency	20	15000	SutherlandHodgman	SimpleSkyDiffuseModeling	InternalCalculation	No	No	No

ZoneInfiltration Airflow Stats Nominal
	Name	Schedule Name	Zone Name	Zone Floor Area {m2}	# Zone Occupants	Design Volume Flow Rate {m3/s}	Volume Flow Rate/Floor Area {m3/s-m2}	Volume Flow Rate/Exterior Surface Area {m3/s-m2}	ACH - Air Changes per Hour	Equation A - Constant Term Coefficient {}	Equation B - Temperature Term Coefficient {1/C}	Equation C - Velocity Term Coefficient {s/m}	Equation D - Velocity Squared Term Coefficient {s2/m2}
1	SPACE1-1 INFIL 1	INFIL-SCH	SPACE1-1	99.16	11.0	3.200E-002	3.227E-004	4.372E-004	0.482	0.000	0.000	0.224	0.000
2	SPACE2-1 INFIL 1	INFIL-SCH	SPACE2-1	42.74	5.0	1.400E-002	3.276E-004	3.838E-004	0.488	0.000	0.000	0.224	0.000
3	SPACE3-1 INFIL 1	INFIL-SCH	SPACE3-1	96.48	11.0	3.200E-002	3.317E-004	4.372E-004	0.482	0.000	0.000	0.224	0.000
4	SPACE4-1 INFIL 1	INFIL-SCH	SPACE4-1	42.74	5.0	1.400E-002	3.276E-004	3.838E-004	0.488	0.000	0.000	0.224	0.000
5	SPACE5-1 INFIL 1	INFIL-SCH	SPACE5-1	182.49	20.0	6.200E-002	3.397E-004	N/A	0.499	0.000	0.000	0.224	0.000

AirFlow Model
	Simple
1	Simple

RoomAir Model
	Zone Name	Mixing/Mundt/UCSDDV/UCSDCV/UCSDUFI/UCSDUFE/User Defined
1	PLENUM-1	Mixing/Well-Stirred
2	SPACE1-1	Mixing/Well-Stirred
3	SPACE2-1	Mixing/Well-Stirred
4	SPACE3-1	Mixing/Well-Stirred
5	SPACE4-1	Mixing/Well-Stirred
6	SPACE5-1	Mixing/Well-Stirred

AirflowNetwork Model:Control
	No Multizone or Distribution/Multizone with Distribution/Multizone without Distribution/Multizone with Distribution only during Fan Operation
1	NoMultizoneOrDistribution

Zone Volume Capacitance Multiplier
	Sensible Heat Capacity Multiplier	Moisture Capacity Multiplier	Carbon Dioxide Capacity Multiplier	Generic Contaminant Capacity Multiplier
1	1.000	1.000	1.000	1.000

Load Timesteps in Zone Design Calculation Averaging Window
	Value
1	4

Heating Sizing Factor Information
	Sizing Factor ID	Value
1	Global	1.3000
2	Zone SPACE1-1	1.3000
3	Zone SPACE2-1	1.3000
4	Zone SPACE3-1	1.3000
5	Zone SPACE4-1	1.3000
6	Zone SPACE5-1	1.3000

Cooling Sizing Factor Information
	Sizing Factor ID	Value
1	Global	1.3000
2	Zone SPACE1-1	1.3000
3	Zone SPACE2-1	1.3000
4	Zone SPACE3-1	1.3000
5	Zone SPACE4-1	1.3000
6	Zone SPACE5-1	1.3000

Zone Sizing Information
	Zone Name	Load Type	Calc Des Load {W}	User Des Load {W}	Calc Des Air Flow Rate {m3/s}	User Des Air Flow Rate {m3/s}	Design Day Name	Date/Time of Peak	Temperature at Peak {C}	Humidity Ratio at Peak {kgWater/kgDryAir}	Floor Area {m2}	# Occupants	Calc Outdoor Air Flow Rate {m3/s}	Calc DOAS Heat Addition Rate {W}
1	SPACE1-1	Cooling	2340.53436	3042.69467	0.20400	0.26520	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	31.50000	1.45947E-002	99.16000	11.00000	0.10384	0.00000
2	SPACE1-1	Heating	3860.76475	5018.99417	0.12090	0.15717	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	-17.30000	8.38927E-004	99.16000	11.00000	0.10384	0.00000
3	SPACE2-1	Cooling	1332.78565	1732.62134	0.11617	0.15102	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 10:00:00	27.43400	1.45947E-002	42.73500	5.00000	4.72000E-002	0.00000
4	SPACE2-1	Heating	1625.14886	2112.69352	5.08904E-002	6.61575E-002	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	-17.30000	8.38927E-004	42.73500	5.00000	4.72000E-002	0.00000
5	SPACE3-1	Cooling	4609.97106	5992.96238	0.40178	0.52232	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 10:45:00	28.63775	1.45947E-002	96.48000	11.00000	0.10384	0.00000
6	SPACE3-1	Heating	3753.06885	4878.98951	0.11752	0.15278	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	-17.30000	8.38927E-004	96.48000	11.00000	0.10384	0.00000
7	SPACE4-1	Cooling	2751.72433	3577.24162	0.23984	0.31179	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 16:45:00	30.21600	1.45947E-002	42.73500	5.00000	4.72000E-002	0.00000
8	SPACE4-1	Heating	1625.14886	2112.69352	5.08904E-002	6.61575E-002	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	-17.30000	8.38927E-004	42.73500	5.00000	4.72000E-002	0.00000
9	SPACE5-1	Cooling	2604.98560	3386.48128	0.22706	0.29518	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	31.50000	1.45947E-002	182.49000	20.00000	0.18880	0.00000
10	SPACE5-1	Heating	2981.56778	3876.03811	9.33652E-002	0.18880	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	-17.30000	8.38927E-004	182.49000	20.00000	0.18880	0.00000

System Sizing Information
	System Name	Load Type	Peak Load Kind	User Design Capacity	Calc Des Air Flow Rate [m3/s]	User Des Air Flow Rate [m3/s]	Design Day Name	Date/Time of Peak
1	VAV SYS 1	Cooling	Sensible	24200.66	1.54550	1.54550	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 00:00:00
2	VAV SYS 1	Heating	Sensible	18125.61	0.63106	0.63106	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 01:00:00

Component Sizing Information
	Component Type	Component Name	Input Field Description	Value
1	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Maximum Air Flow Rate [m3/s]	0.26520
2	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Constant Minimum Air Flow Fraction	0.28492
3	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	User-Specified Constant Minimum Air Flow Fraction	0.40000
4	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Minimum Air Flow Rate [m3/s]	0.10608
5	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Maximum Flow Fraction during Reheat []	0.75979
6	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00203
7	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Maximum Reheat Water Flow Rate [m3/s]	0.00013
8	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Reheat Coil Sizing Air Volume Flow Rate [m3/s]	0.15717
9	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Temperature [C]	16.70000
10	AirTerminal:SingleDuct:VAV:Reheat	SPACE1-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Humidity Ratio [kgWater/kgDryAir]	0.00800
11	Coil:Heating:Water	SPACE1-1 ZONE COIL	Design Size Rated Capacity [W]	6011.32729
12	Coil:Heating:Water	SPACE1-1 ZONE COIL	Design Size Maximum Water Flow Rate [m3/s]	0.00013
13	Coil:Heating:Water	SPACE1-1 ZONE COIL	Design Size U-Factor Times Area Value [W/K]	147.21716
14	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Maximum Air Flow Rate [m3/s]	0.15102
15	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Constant Minimum Air Flow Fraction	0.21563
16	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	User-Specified Constant Minimum Air Flow Fraction	0.40000
17	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Minimum Air Flow Rate [m3/s]	0.06041
18	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Maximum Flow Fraction during Reheat []	0.93747
19	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00331
20	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Maximum Reheat Water Flow Rate [m3/s]	0.00006
21	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Reheat Coil Sizing Air Volume Flow Rate [m3/s]	0.06616
22	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Temperature [C]	16.70000
23	AirTerminal:SingleDuct:VAV:Reheat	SPACE2-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Humidity Ratio [kgWater/kgDryAir]	0.00800
24	Coil:Heating:Water	SPACE2-1 ZONE COIL	Design Size Rated Capacity [W]	2530.40426
25	Coil:Heating:Water	SPACE2-1 ZONE COIL	Design Size Maximum Water Flow Rate [m3/s]	0.00006
26	Coil:Heating:Water	SPACE2-1 ZONE COIL	Design Size U-Factor Times Area Value [W/K]	61.96942
27	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Maximum Air Flow Rate [m3/s]	0.52232
28	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Constant Minimum Air Flow Fraction	0.20000
29	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	User-Specified Constant Minimum Air Flow Fraction	0.40000
30	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Minimum Air Flow Rate [m3/s]	0.20893
31	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Maximum Flow Fraction during Reheat []	0.40000
32	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00217
33	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Maximum Reheat Water Flow Rate [m3/s]	0.00014
34	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Reheat Coil Sizing Air Volume Flow Rate [m3/s]	0.20893
35	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Temperature [C]	16.70000
36	AirTerminal:SingleDuct:VAV:Reheat	SPACE3-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Humidity Ratio [kgWater/kgDryAir]	0.00800
37	Coil:Heating:Water	SPACE3-1 ZONE COIL	Design Size Rated Capacity [W]	6198.12303
38	Coil:Heating:Water	SPACE3-1 ZONE COIL	Design Size Maximum Water Flow Rate [m3/s]	0.00014
39	Coil:Heating:Water	SPACE3-1 ZONE COIL	Design Size U-Factor Times Area Value [W/K]	137.94576
40	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Maximum Air Flow Rate [m3/s]	0.31179
41	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Constant Minimum Air Flow Fraction	0.20000
42	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	User-Specified Constant Minimum Air Flow Fraction	0.40000
43	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Minimum Air Flow Rate [m3/s]	0.12471
44	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Maximum Flow Fraction during Reheat []	0.45408
45	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00331
46	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Maximum Reheat Water Flow Rate [m3/s]	0.00006
47	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Reheat Coil Sizing Air Volume Flow Rate [m3/s]	0.12471
48	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Temperature [C]	16.70000
49	AirTerminal:SingleDuct:VAV:Reheat	SPACE4-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Humidity Ratio [kgWater/kgDryAir]	0.00800
50	Coil:Heating:Water	SPACE4-1 ZONE COIL	Design Size Rated Capacity [W]	2900.12536
51	Coil:Heating:Water	SPACE4-1 ZONE COIL	Design Size Maximum Water Flow Rate [m3/s]	0.00006
52	Coil:Heating:Water	SPACE4-1 ZONE COIL	Design Size U-Factor Times Area Value [W/K]	60.79707
53	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Maximum Air Flow Rate [m3/s]	0.29518
54	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Constant Minimum Air Flow Fraction	0.47110
55	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	User-Specified Constant Minimum Air Flow Fraction	0.40000
56	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Minimum Air Flow Rate [m3/s]	0.11807
57	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Maximum Flow Fraction during Reheat []	1.00000
58	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2]	0.00162
59	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Maximum Reheat Water Flow Rate [m3/s]	0.00010
60	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Reheat Coil Sizing Air Volume Flow Rate [m3/s]	0.12137
61	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Temperature [C]	16.70000
62	AirTerminal:SingleDuct:VAV:Reheat	SPACE5-1 VAV REHEAT	Design Size Reheat Coil Sizing Inlet Air Humidity Ratio [kgWater/kgDryAir]	0.00800
63	Coil:Heating:Water	SPACE5-1 ZONE COIL	Design Size Rated Capacity [W]	4641.97211
64	Coil:Heating:Water	SPACE5-1 ZONE COIL	Design Size Maximum Water Flow Rate [m3/s]	0.00010
65	Coil:Heating:Water	SPACE5-1 ZONE COIL	Design Size U-Factor Times Area Value [W/K]	113.67705
66	AirLoopHVAC	VAV SYS 1	Sum of Air Terminal Maximum Heating Flow Rates [m3/s]	0.98875
67	AirLoopHVAC	VAV SYS 1	Sum of Air Terminal Minimum Heating Flow Rates [m3/s]	0.61820
68	AirLoopHVAC	VAV SYS 1	Sum of Air Terminal Maximum Flow Rates [m3/s]	1.54550
69	AirLoopHVAC	VAV SYS 1	Adjusted Heating Design Air Flow Rate [m3/s]	0.98875
70	AirLoopHVAC	VAV SYS 1	Adjusted Cooling Design Air Flow Rate [m3/s]	1.54550
71	AirLoopHVAC	VAV SYS 1	Adjusted Main Design Air Flow Rate [m3/s]	1.54550
72	AirLoopHVAC	VAV SYS 1	User Heating Air Flow Ratio []	0.30000
73	AirLoopHVAC	VAV SYS 1	Calculated Heating Air Flow Ratio []	0.63976
74	AirLoopHVAC	VAV SYS 1	Design Supply Air Flow Rate [m3/s]	1.54550
75	Controller:OutdoorAir	OA CONTROLLER 1	Maximum Outdoor Air Flow Rate [m3/s]	1.54550
76	Controller:OutdoorAir	OA CONTROLLER 1	Minimum Outdoor Air Flow Rate [m3/s]	0.49088
77	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Inlet Air Temperature [C]	26.53269
78	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Inlet Water Temperature [C]	7.22000
79	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Outlet Air Temperature [C]	12.06361
80	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Inlet Air Humidity Ratio	0.01126
81	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Outlet Air Humidity Ratio	0.00800
82	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Coil Load [W]	40439.25741
83	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Water Flow Rate [m3/s]	0.00144
84	Coil:Cooling:Water	MAIN COOLING COIL 1	Design Size Design Air Flow Rate [m3/s]	1.54550
85	Coil:Heating:Water	MAIN HEATING COIL 1	Design Size Rated Capacity [W]	17975.11765
86	Coil:Heating:Water	MAIN HEATING COIL 1	Design Size Maximum Water Flow Rate [m3/s]	0.00040
87	Coil:Heating:Water	MAIN HEATING COIL 1	Design Size U-Factor Times Area Value [W/K]	241.47290
88	Fan:VariableVolume	SUPPLY FAN 1	Design Size Maximum Flow Rate [m3/s]	1.54550
89	Controller:WaterCoil	CENTRAL COOLING COIL CONTOLLER 1	Maximum Actuated Flow [m3/s]	0.00144
90	Controller:WaterCoil	CENTRAL HEATING COIL CONTOLLER 1	Maximum Actuated Flow [m3/s]	0.00040
91	PlantLoop	HOT WATER LOOP	Maximum Loop Flow Rate [m3/s]	0.00089
92	PlantLoop	HOT WATER LOOP	Plant Loop Volume [m3]	0.10673
93	Pump:VariableSpeed	HW CIRC PUMP	Design Flow Rate [m3/s]	0.00089
94	Pump:VariableSpeed	HW CIRC PUMP	Design Power Consumption [W]	227.23815
95	Boiler:HotWater	CENTRAL BOILER	Design Size Nominal Capacity [W]	40257.06970
96	Boiler:HotWater	CENTRAL BOILER	Design Size Design Water Flow Rate [m3/s]	0.00089
97	PlantLoop	CHILLED WATER LOOP	Maximum Loop Flow Rate [m3/s]	0.00144
98	PlantLoop	CHILLED WATER LOOP	Plant Loop Volume [m3]	0.17333
99	Pump:VariableSpeed	CW CIRC PUMP	Design Flow Rate [m3/s]	0.00144
100	Pump:VariableSpeed	CW CIRC PUMP	Design Power Consumption [W]	369.02480
101	Chiller:Electric	CENTRAL CHILLER	Design Size Nominal Capacity [W]	40439.25741
102	Chiller:Electric	CENTRAL CHILLER	Design Size Design Chilled Water Flow Rate [m3/s]	0.00144
103	Chiller:Electric	CENTRAL CHILLER	User-Specified Design Condenser Water Flow Rate [m3/s]	0.00110

Water Heating Coil Capacity Information
	Component Type	Name	Nominal Total Capacity {W}
1	Coil:Heating:Water	SPACE1-1 ZONE COIL	6042.82
2	Coil:Heating:Water	SPACE2-1 ZONE COIL	2543.66
3	Coil:Heating:Water	SPACE3-1 ZONE COIL	6233.45
4	Coil:Heating:Water	SPACE4-1 ZONE COIL	2917.49
5	Coil:Heating:Water	SPACE5-1 ZONE COIL	4666.29
6	Coil:Heating:Water	MAIN HEATING COIL 1	11910.04

Water Cooling Coil Capacity Information
	Component Type	Name	Nominal Total Capacity {W}	Nominal Sensible Capacity {W}	Nominal Latent Capacity {W}	Nominal Sensible Heat Ratio	Nominal Coil UA Value {W/C}	Nominal Coil Surface Area {m2}
1	Coil:Cooling:Water	MAIN COOLING COIL 1	46001.07	28722.66	17278.41	0.62	6467.30	65.59

Environment
	Environment Name	Environment Type	Start Date	End Date	Start DayOfWeek	Duration {#days}	Source:Start DayOfWeek	Use Daylight Saving	Use Holidays	Apply Weekend Holiday Rule	Use Rain Values	Use Snow Values
1	RUNPERIOD 1	WeatherFileRunPeriod	01/01/2013	12/31/2013	Tuesday	365	Use RunPeriod Specified Day	Yes	Yes	No	Yes	Yes

Environment:Daylight Saving
	Daylight Saving Indicator	Source	Start Date	End Date
1	No

Environment:WarmupDays
	NumberofWarmupDays
1	6

Tabular Report
	Style	Unit Conversion
1	HTML	JTOKWH

Warmup Convergence Information
	Zone Name	Environment Type/Name	Average Warmup Temperature Difference {deltaC}	Std Dev Warmup Temperature Difference {deltaC}	Max Temperature Pass/Fail Convergence	Min Temperature Pass/Fail Convergence	Average Warmup Load Difference {W}	Std Dev Warmup Load Difference {W}	Heating Load Pass/Fail Convergence	Cooling Load Pass/Fail Convergence
1	PLENUM-1	RunPeriod: RUNPERIOD 1	0.1026500884	8.4974482944E-002	Pass	Pass	0.1695512770	0.4820628912	Pass	Pass
2	SPACE1-1	RunPeriod: RUNPERIOD 1	6.3180999433E-002	0.1339279307	Pass	Pass	0.2059210772	0.8966172621	Pass	Pass
3	SPACE2-1	RunPeriod: RUNPERIOD 1	6.3321313330E-002	0.1391757494	Pass	Pass	0.2120168816	0.8894661820	Pass	Pass
4	SPACE3-1	RunPeriod: RUNPERIOD 1	6.2732990381E-002	0.1224947758	Pass	Pass	0.1998144705	0.7719520461	Pass	Pass
5	SPACE4-1	RunPeriod: RUNPERIOD 1	5.7160455207E-002	0.1084543788	Pass	Pass	0.1965442178	0.7754375068	Pass	Pass
6	SPACE5-1	RunPeriod: RUNPERIOD 1	6.3943581089E-002	0.1566892840	Pass	Pass	0.1682951812	0.5620296325	Pass	Pass

Table of Contents
Report: Annual Heat Emissions Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Heat Emission by Components
	Envelope Convection	Zone Exfiltration	Zone Exhaust Air	HVAC Relief Air	HVAC Reject Heat	Total
Heat Emissions [GJ]	2309.62	-0.7	0.00	-27.6	236.47	2517.77

Table of Contents
Report: Climatic Data Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
SizingPeriod:DesignDay
	Maximum Dry Bulb [C]	Daily Temperature Range [deltaC]	Humidity Value	Humidity Type	Wind Speed [m/s]	Wind Direction
CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	-17.30	0.00	-17.30	Wetbulb [C]	4.90	270.00
CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	31.50	10.70	23.00	Wetbulb [C]	5.30	230.00

Weather Statistics File
	Value
None

Table of Contents
Report: Envelope Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Opaque Exterior
	Construction	Reflectance	U-Factor with Film [W/m2-K]	U-Factor no Film [W/m2-K]	Gross Area [m2]	Net Area [m2]	Azimuth [deg]	Tilt [deg]	Cardinal Direction
WALL-1PF	WALL-1	0.22	0.384	0.408	18.30	18.30	210.00	90.00	S
WALL-1PR	WALL-1	0.22	0.384	0.408	9.12	9.12	120.00	90.00	E
WALL-1PB	WALL-1	0.22	0.384	0.408	18.30	18.30	30.00	90.00	N
WALL-1PL	WALL-1	0.22	0.384	0.408	9.12	9.12	300.00	90.00	W
TOP-1	ROOF-1	0.35	0.271	0.282	463.60	463.60	210.00	0.00
FRONT-1	WALL-1	0.22	0.384	0.408	73.20	51.39	210.00	90.00	S
F1-1	FLOOR-SLAB-1	0.35	4.174	12.894	99.16	99.16	30.00	180.00
RIGHT-1	WALL-1	0.22	0.384	0.408	36.48	27.36	120.00	90.00	E
F2-1	FLOOR-SLAB-1	0.35	4.174	12.894	42.73	42.73	300.00	180.00
BACK-1	WALL-1	0.22	0.384	0.408	73.20	52.35	30.00	90.00	N
F3-1	FLOOR-SLAB-1	0.35	4.174	12.894	96.48	96.48	74.22	180.00
LEFT-1	WALL-1	0.22	0.384	0.408	36.48	27.36	300.00	90.00	W
F4-1	FLOOR-SLAB-1	0.35	4.174	12.894	42.73	42.73	120.00	180.00
F5-1	FLOOR-SLAB-1	0.35	4.174	12.894	182.49	182.49	30.00	180.00

Exterior Fenestration
	Construction	Glass Area [m2]	Frame Area [m2]	Divider Area [m2]	Area of One Opening [m2]	Area of Multiplied Openings [m2]	Glass U-Factor [W/m2-K]	Glass SHGC	Glass Visible Transmittance	Frame Conductance [W/m2-K]	Divider Conductance [W/m2-K]	Shade Control	Parent Surface	Azimuth [deg]	Tilt [deg]	Cardinal Direction
WF-1	DBL CLR 3MM/13MM AIR	16.56	0.00	0.00	16.56	16.56	2.720	0.764	0.812			No	FRONT-1	210.00	90.00	S
DF-1	SGL GREY 3MM	5.25	0.00	0.00	5.25	5.25	5.894	0.716	0.611			No	FRONT-1	210.00	90.00	S
WR-1	DBL CLR 3MM/13MM AIR	9.12	0.00	0.00	9.12	9.12	2.720	0.764	0.812			No	RIGHT-1	120.00	90.00	E
WB-1	DBL CLR 3MM/13MM AIR	16.44	0.00	0.00	16.44	16.44	2.720	0.764	0.812			No	BACK-1	30.00	90.00	N
DB-1	SGL GREY 3MM	4.41	0.00	0.00	4.41	4.41	5.894	0.716	0.611			No	BACK-1	30.00	90.00	N
WL-1	DBL CLR 3MM/13MM AIR	9.12	0.00	0.00	9.12	9.12	2.720	0.764	0.812			No	LEFT-1	300.00	90.00	W
Total or Average						60.90	3.223	0.756	0.780
North Total or Average						20.85	3.391	0.754	0.769
Non-North Total or Average						40.05	3.136	0.757	0.785

Interior Fenestration
	Construction	Area of One Opening [m2]	Area of Openings [m2]	Glass U-Factor [W/m2-K]	Glass SHGC	Glass Visible Transmittance	Parent Surface
Total or Average			0.00	-	-	-

Exterior Door
	Construction	U-Factor with Film [W/m2-K]	U-Factor no Film [W/m2-K]	Gross Area [m2]	Parent Surface
None

Table of Contents
Report: Shading Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Sunlit Fraction
	March 21 9am	March 21 noon	March 21 3pm	June 21 9am	June 21 noon	June 21 3pm	December 21 9am	December 21 noon	December 21 3pm
WF-1	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
DF-1	0.00	0.00	0.30	0.00	0.00	0.00	0.00	0.04	0.36
WR-1	1.00	1.00	0.00	1.00	0.00	0.00	1.00	1.00	0.00
WB-1	1.00	1.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00
DB-1	1.00	1.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00
WL-1	0.00	0.00	1.00	0.00	1.00	1.00	0.00	0.00	1.00

Window Control
	Name	Type	Shaded Construction	Control	Glare Control
None

Table of Contents
Report: Lighting Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Interior Lighting
	Zone	Lighting Power Density [W/m2]	Zone Area [m2]	Total Power [W]	End Use Subcategory	Schedule Name	Scheduled Hours/Week [hr]	Hours/Week > 1% [hr]	Full Load Hours/Week [hr]	Return Air Fraction	Conditioned (Y/N)	Consumption [kWh]
SPACE1-1 LIGHTS 1	SPACE1-1	15.9742	99.16	1584.00	GeneralLights	LIGHTS-1	57.70	168.00	57.70	0.2000	Y	4766.00
SPACE2-1 LIGHTS 1	SPACE2-1	16.0056	42.73	684.00	GeneralLights	LIGHTS-1	57.70	168.00	57.70	0.2000	Y	2058.05
SPACE3-1 LIGHTS 1	SPACE3-1	16.4179	96.48	1584.00	GeneralLights	LIGHTS-1	57.70	168.00	57.70	0.2000	Y	4766.00
SPACE4-1 LIGHTS 1	SPACE4-1	16.0056	42.73	684.00	GeneralLights	LIGHTS-1	57.70	168.00	57.70	0.2000	Y	2058.05
SPACE5-1 LIGHTS 1	SPACE5-1	16.2420	182.49	2964.00	GeneralLights	LIGHTS-1	57.70	168.00	57.70	0.2000	Y	8918.20
Interior Lighting Total		16.1777	463.60	7500.00								22566.30

Daylighting
	Zone	Control Name	Daylighting Method	Control Type	Fraction Controlled	Lighting Installed in Zone [W]	Lighting Controlled [W]
None

Exterior Lighting
	Total Watts	Astronomical Clock/Schedule	Schedule Name	Scheduled Hours/Week [hr]	Hours/Week > 1% [hr]	Full Load Hours/Week [hr]	Consumption [kWh]
Exterior Lighting Total	0.00						0.00

Table of Contents
Report: Equipment Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Central Plant
	Type	Nominal Capacity [W]	Nominal Efficiency [W/W]	IPLV in SI Units [W/W]	IPLV in IP Units [Btu/W-h]
CENTRAL BOILER	Boiler:HotWater	40257.07	0.80
CENTRAL CHILLER	Chiller:Electric	40439.26	3.20

Cooling Coils
	Type	Design Coil Load [W]	Nominal Total Capacity [W]	Nominal Sensible Capacity [W]	Nominal Latent Capacity [W]	Nominal Sensible Heat Ratio	Nominal Efficiency [W/W]	Nominal Coil UA Value [W/C]	Nominal Coil Surface Area [m2]
MAIN COOLING COIL 1	Coil:Cooling:Water	40439.26	46001.07	28722.66	17278.41	0.62	-	6467.30	65.59

Nominal values are gross at rated conditions, i.e., the supply air fan heat and electric power NOT accounted for.
DX Cooling Coils
	DX Cooling Coil Type	Standard Rated Net Cooling Capacity [W]	Standard Rated Net COP [W/W]	EER [Btu/W-h]	SEER [Btu/W-h]	IEER [Btu/W-h]
None

DX Cooling Coil ASHRAE 127 Standard Ratings Report
	DX Cooling Coil Type	Rated Net Cooling Capacity Test A [W]	Rated Electric Power Test A [W]	Rated Net Cooling Capacity Test B [W]	Rated Electric Power Test B [W]	Rated Net Cooling Capacity Test C [W]	Rated Electric Power Test C [W]	Rated Net Cooling Capacity Test D [W]	Rated Electric Power Test D [W]
None

DX Heating Coils
	DX Heating Coil Type	High Temperature Heating (net) Rating Capacity [W]	Low Temperature Heating (net) Rating Capacity [W]	HSPF [Btu/W-h]	Region Number
None

Heating Coils
	Type	Design Coil Load [W]	Nominal Total Capacity [W]	Nominal Efficiency [W/W]
SPACE1-1 ZONE COIL	Coil:Heating:Water	6011.33	6042.82	-
SPACE2-1 ZONE COIL	Coil:Heating:Water	2530.40	2543.66	-
SPACE3-1 ZONE COIL	Coil:Heating:Water	6198.12	6233.45	-
SPACE4-1 ZONE COIL	Coil:Heating:Water	2900.13	2917.49	-
SPACE5-1 ZONE COIL	Coil:Heating:Water	4641.97	4666.29	-
MAIN HEATING COIL 1	Coil:Heating:Water	17975.12	11910.04	-

Nominal values are gross at rated conditions, i.e., the supply air fan heat and electric power NOT accounted for.
Fans
	Type	Total Efficiency [W/W]	Delta Pressure [pa]	Max Air Flow Rate [m3/s]	Rated Electric Power [W]	Rated Power Per Max Air Flow Rate [W-s/m3]	Motor Heat In Air Fraction	Fan Energy Index	End Use Subcategory	Design Day Name for Fan Sizing Peak	Date/Time for Fan Sizing Peak
SUPPLY FAN 1	Fan:VariableVolume	0.70	600.00	1.55	1324.71	857.14	1.00	1.63	General	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:15:00

Pumps
	Type	Control	Head [pa]	Water Flow [m3/s]	Electric Power [W]	Power Per Water Flow Rate [W-s/m3]	Motor Efficiency [W/W]	End Use Subcategory
HW CIRC PUMP	Pump:VariableSpeed	Intermittent	179352.00	0.000889	227.24	255487.18	0.90	General
CW CIRC PUMP	Pump:VariableSpeed	Intermittent	179352.00	0.001444	369.02	255487.18	0.90	General

Service Water Heating
	Type	Storage Volume [m3]	Input [W]	Thermal Efficiency [W/W]	Recovery Efficiency [W/W]	Energy Factor
None

Table of Contents
Report: HVAC Sizing Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Zone Sensible Cooling
	Calculated Design Load [W]	User Design Load [W]	User Design Load per Area [W/m2]	Calculated Design Air Flow [m3/s]	User Design Air Flow [m3/s]	Design Day Name	Date/Time Of Peak {TIMESTAMP}	Thermostat Setpoint Temperature at Peak Load [C]	Indoor Temperature at Peak Load [C]	Indoor Humidity Ratio at Peak Load [kgWater/kgAir]	Outdoor Temperature at Peak Load [C]	Outdoor Humidity Ratio at Peak Load [kgWater/kgAir]	Minimum Outdoor Air Flow Rate [m3/s]	Heat Gain Rate from DOAS [W]
SPACE1-1	2340.53	3042.69	30.68	0.204	0.265	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	23.90	23.90	0.00986	31.50	0.01459	0.104	0.00
SPACE2-1	1332.79	1732.62	40.54	0.116	0.151	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 10:00:00	23.90	23.90	0.00972	27.43	0.01459	0.047	0.00
SPACE3-1	4609.97	5992.96	62.12	0.402	0.522	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 10:45:00	23.90	23.90	0.00945	28.64	0.01459	0.104	0.00
SPACE4-1	2751.72	3577.24	83.71	0.240	0.312	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 16:45:00	23.90	23.90	0.00934	30.22	0.01459	0.047	0.00
SPACE5-1	2604.99	3386.48	18.56	0.227	0.295	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	23.90	23.90	0.01037	31.50	0.01459	0.189	0.00

The Design Load is the zone sensible load only. It does not include any system effects or ventilation loads.
Zone Sensible Heating
	Calculated Design Load [W]	User Design Load [W]	User Design Load per Area [W/m2]	Calculated Design Air Flow [m3/s]	User Design Air Flow [m3/s]	Design Day Name	Date/Time Of Peak {TIMESTAMP}	Thermostat Setpoint Temperature at Peak Load [C]	Indoor Temperature at Peak Load [C]	Indoor Humidity Ratio at Peak Load [kgWater/kgAir]	Outdoor Temperature at Peak Load [C]	Outdoor Humidity Ratio at Peak Load [kgWater/kgAir]	Minimum Outdoor Air Flow Rate [m3/s]	Heat Gain Rate from DOAS [W]
SPACE1-1	3860.76	5018.99	50.62	0.121	0.157	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	22.20	22.20	0.00377	-17.30	0.00084	0.104	0.00
SPACE2-1	1625.15	2112.69	49.44	0.051	0.066	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	22.20	22.20	0.00377	-17.30	0.00084	0.047	0.00
SPACE3-1	3753.07	4878.99	50.57	0.118	0.153	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	22.20	22.20	0.00377	-17.30	0.00084	0.104	0.00
SPACE4-1	1625.15	2112.69	49.44	0.051	0.066	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	22.20	22.20	0.00377	-17.30	0.00084	0.047	0.00
SPACE5-1	2981.57	3876.04	21.24	0.093	0.189	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	22.20	22.20	0.00349	-17.30	0.00084	0.189	0.00

The Design Load is the zone sensible load only. It does not include any system effects or ventilation loads.
System Design Air Flow Rates
	Calculated cooling [m3/s]	User cooling [m3/s]	Calculated heating [m3/s]	User heating [m3/s]	Adjusted cooling [m3/s]	Adjusted heating [m3/s]	Adjusted main [m3/s]	Calculated Heating Air Flow Ratio []	User Heating Air Flow Ratio []
VAV SYS 1	1.55	1.55	0.63	0.63	1.5455	0.9887	1.5455	0.6398	0.3000

Plant Loop Coincident Design Fluid Flow Rate Adjustments
	Previous Design Volume Flow Rate [m3/s]	Algorithm Volume Flow Rate [m3/s]	Coincident Design Volume Flow Rate [m3/s]	Coincident Size Adjusted	Peak Sizing Period Name	Peak Day into Period {TIMESTAMP}[day]	Peak Hour Of Day {TIMESTAMP}[hr]	Peak Step Start Minute {TIMESTAMP}[min]
None

Coil Sizing Summary
	Coil Type	HVAC Type	HVAC Name	Coil Final Gross Total Capacity [W]	Coil Final Gross Sensible Capacity [W]	Coil Final Reference Air Volume Flow Rate [m3/s]	Coil Final Reference Plant Fluid Volume Flow Rate [m3/s]	Coil U-value Times Area Value [W/K]	Design Day Name at Sensible Ideal Loads Peak	Date/Time at Sensible Ideal Loads Peak	Design Day Name at Air Flow Ideal Loads Peak	Date/Time at Air Flow Ideal Loads Peak	Coil Total Capacity at Ideal Loads Peak [W]	Coil Sensible Capacity at Ideal Loads Peak [W]	Coil Air Volume Flow Rate at Ideal Loads Peak [m3/s]	Coil Entering Air Drybulb at Ideal Loads Peak [C]	Coil Entering Air Wetbulb at Ideal Loads Peak [C]	Coil Entering Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Coil Leaving Air Drybulb at Ideal Loads Peak [C]	Coil Leaving Air Wetbulb at Ideal Loads Peak [C]	Coil Leaving Air Humidity Ratio at Ideal Loads Peak [C]	Outdoor Air Drybulb at Ideal Loads Peak [C]	Outdoor Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Outdoor Air Wetbulb at Ideal Loads Peak [C]	Outdoor Air Flow Percentage at Ideal Loads Peak [%]	Zone Air Drybulb at Ideal Loads Peak [C]	Zone Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Zone Air Relative Humidity at Ideal Loads Peak [%]	Zone Sensible Heat Gain at Ideal Loads Peak [W]	Zone Latent Heat Gain at Ideal Loads Peak [W]	Coil Total Capacity at Rating Conditions [W]	Coil Sensible Capacity at Rating Conditions [W]
SPACE1-1 ZONE COIL	COIL:HEATING:WATER	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE1-1 ATU	6011.327	6011.327	0.157166	0.00013281	147.217	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	6042.82	6011.33	0.157166	16.70	12.63	0.00800000	50.00	20.50	0.00400000	-17.30	0.00083893	-17.37	0.0000	22.20	0.00377474	21.5133	5018.99	0.00	6048.59	6048.59
SPACE2-1 ZONE COIL	COIL:HEATING:WATER	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE2-1 ATU	2530.404	2530.404	0.066158	0.00005591	61.969	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	2543.66	2530.40	0.066158	16.70	12.63	0.00800000	50.00	20.50	0.00400000	-17.30	0.00083893	-17.37	0.0000	22.20	0.00376653	21.4668	2112.69	0.00	2546.09	2546.09
SPACE3-1 ZONE COIL	COIL:HEATING:WATER	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE3-1 ATU	6198.123	6198.123	0.208927	0.00013694	137.946	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	6233.45	6198.12	0.208927	16.70	12.63	0.00800000	50.00	20.50	0.00400000	-17.30	0.00083893	-17.37	0.0000	22.20	0.00376874	21.4794	4878.99	0.00	6237.66	6237.66
SPACE4-1 ZONE COIL	COIL:HEATING:WATER	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE4-1 ATU	2900.125	2900.125	0.124714	0.00006407	60.797	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	2917.49	2900.13	0.124714	16.70	12.63	0.00800000	50.00	20.50	0.00400000	-17.30	0.00083893	-17.37	0.0000	22.20	0.00376653	21.4668	2112.69	0.00	2918.91	2918.91
SPACE5-1 ZONE COIL	COIL:HEATING:WATER	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE5-1 ATU	4641.972	4641.972	0.121375	0.00010256	113.677	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	4666.29	4641.97	0.121375	16.70	12.63	0.00800000	50.00	20.50	0.00400000	-17.30	0.00083893	-17.37	0.0000	22.20	0.00348972	19.8981	3876.04	0.00	4670.75	4670.75
MAIN COOLING COIL 1	Coil:Cooling:Water	AirLoopHVAC	VAV SYS 1	40439.257	-999.000	1.545497	0.00144440	-999.000	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:15:00	40439.26	27195.60	1.545497	26.53	18.80	0.01125633	12.06	10.76	0.00800000	29.88	0.01459469	22.11	31.7619	23.90	0.00970247	49.4280	17732.00	0.00	42387.06	28165.59
MAIN HEATING COIL 1	Coil:Heating:Water	AirLoopHVAC	VAV SYS 1	17975.118	17975.118	0.463649	0.00039714	241.473	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 01:00:00	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	11910.04	13513.94	0.463649	-8.49	-9.32	0.00147143	16.70	12.63	0.00800000	-17.30	0.00083893	-17.37	105.8732	22.20	0.00368629	21.0123	17999.41	0.00	11888.97	11888.97

Table of Contents
Report: Coil Sizing Details
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Coils
	Coil Type	Coil Location	HVAC Type	HVAC Name	Zone Name(s)	System Sizing Method Concurrence	System Sizing Method Capacity	System Sizing Method Air Flow	Autosized Coil Capacity?	Autosized Coil Airflow?	Autosized Coil Water Flow?	OA Pretreated prior to coil inlet?	Coil Final Gross Total Capacity [W]	Coil Final Gross Sensible Capacity [W]	Coil Final Reference Air Volume Flow Rate [m3/s]	Coil Final Reference Plant Fluid Volume Flow Rate [m3/s]	Coil U-value Times Area Value [W/K]	Terminal Unit Reheat Coil Multiplier	DX Coil Capacity Increase Ratio from Too Low Flow/Capacity Ratio	DX Coil Capacity Decrease Ratio from Too High Flow/Capacity Ratio	Moist Air Heat Capacity [J/kg-K]	Dry Air Heat Capacity [J/kg-K]	Standard Air Density Adjusted for Elevation [kg/m3]	Supply Fan Name for Coil	Supply Fan Type for Coil	Supply Fan Maximum Air Volume Flow Rate [m3/s]	Supply Fan Maximum Air Mass Flow Rate [kg/s]	Plant Name for Coil	Plant Fluid Specific Heat Capacity [J/kg-K]	Plant Fluid Density [kg/m3]	Plant Maximum Fluid Mass Flow Rate [kg/s]	Plant Design Fluid Return Temperature [C]	Plant Design Fluid Supply Temperature [C]	Plant Design Fluid Temperature Difference [deltaC]	Plant Design Capacity [W]	Coil Capacity Percentage of Plant Design Capacity [%]	Coil Fluid Flow Rate Percentage of Plant Design Flow Rate [%]	Design Day Name at Sensible Ideal Loads Peak	Date/Time at Sensible Ideal Loads Peak	Design Day Name at Total Ideal Loads Peak	Date/Time at Total Ideal Loads Peak	Design Day Name at Air Flow Ideal Loads Peak	Date/Time at Air Flow Ideal Loads Peak	Coil Total Capacity at Ideal Loads Peak [W]	Coil Sensible Capacity at Ideal Loads Peak [W]	Coil Off-Rating Capacity Modifier at Ideal Loads Peak [ ]	Coil Air Mass Flow Rate at Ideal Loads Peak [kg/s]	Coil Air Volume Flow Rate at Ideal Loads Peak [m3/s]	Coil Entering Air Drybulb at Ideal Loads Peak [C]	Coil Entering Air Wetbulb at Ideal Loads Peak [C]	Coil Entering Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Coil Entering Air Enthalpy at Ideal Loads Peak [J/KG-K]	Coil Leaving Air Drybulb at Ideal Loads Peak [C]	Coil Leaving Air Wetbulb at Ideal Loads Peak [C]	Coil Leaving Air Humidity Ratio at Ideal Loads Peak [C]	Coil Leaving Air Enthalpy at Ideal Loads Peak [J/KG-K]	Coil Plant Fluid Mass Flow Rate at Ideal Loads Peak [kg/s]	Coil Entering Plant Fluid Temperature at Ideal Loads Peak [C]	Coil Leaving Plant Fluid Temperature at Ideal Loads Peak [C]	Coil Plant Fluid Temperature Difference at Ideal Loads Peak [deltaC]	Supply Fan Air Heat Gain at Ideal Loads Peak [W]	Coil and Fan Net Total Capacity at Ideal Loads Peak [W]	Outdoor Air Drybulb at Ideal Loads Peak [C]	Outdoor Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Outdoor Air Wetbulb at Ideal Loads Peak [C]	Outdoor Air Volume Flow Rate at Ideal Loads Peak [m3/s]	Outdoor Air Flow Percentage at Ideal Loads Peak [%]	System Return Air Drybulb at Ideal Loads Peak [C]	System Return Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Zone Air Drybulb at Ideal Loads Peak [C]	Zone Air Humidity Ratio at Ideal Loads Peak [KGWATER/KGDRYAIR]	Zone Air Relative Humidity at Ideal Loads Peak [%]	Zone Sensible Heat Gain at Ideal Loads Peak [W]	Zone Latent Heat Gain at Ideal Loads Peak [W]	Coil Total Capacity at Rating Conditions [W]	Coil Sensible Capacity at Rating Conditions [W]	Coil Air Mass Flow Rate at Rating Conditions [kg/s]	Coil Entering Air Drybulb at Rating Conditions [C]	Coil Entering Air Wetbulb at Rating Conditions [C]	Coil Entering Air Humidity Ratio at Rating Conditions [KGWATER/KGDRYAIR]	Coil Entering Air Enthalpy at Rating Conditions [J/KG-K]	Coil Leaving Air Drybulb at Rating Conditions [C]	Coil Leaving Air Wetbulb at Rating Conditions [C]	Coil Leaving Air Humidity Ratio at Rating Conditions [KGWATER/KGDRYAIR]	Coil Leaving Air Enthalpy at Rating Conditions [J/KG-K]
SPACE1-1 ZONE COIL	COIL:HEATING:WATER	Zone Equipment	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE1-1 ATU	SPACE1-1	N/A	N/A	N/A	Yes	Yes	Yes	No	6011.327	6011.327	0.157166	0.00013281	147.217	1.0000	1.00000	1.00000	1012.2758	1004.8586	1.1347	unknown	unknown	-999.0	-999.0		4197.9300	999.8980	0.88934003	71.00	82.00	11.00	41067.26	14.7145	14.932352	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	unknown	unknown	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	6042.82	6011.33	1.0000	0.17834336	0.157166	16.70	12.63	0.00800000	37036.7	50.00	20.50	0.00400000	60617.6	0.13279938	60.00	49.00	11.00	0.000	6042.82	-17.30	0.00083893	-17.37	0.00000000	0.0000	22.31	0.00377474	22.20	0.00377474	21.5133	5018.99	0.00	6048.59	6048.59	0.17834336	16.60	13.14	0.00800000	36934.7	49.86	23.91	0.00800000	70850.2
SPACE2-1 ZONE COIL	COIL:HEATING:WATER	Zone Equipment	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE2-1 ATU	SPACE2-1	N/A	N/A	N/A	Yes	Yes	Yes	No	2530.404	2530.404	0.066158	0.00005591	61.969	1.0000	1.00000	1.00000	1012.2758	1004.8586	1.1347	unknown	unknown	-999.0	-999.0		4197.9300	999.8980	0.88934003	71.00	82.00	11.00	41067.26	6.1939	6.285615	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	unknown	unknown	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	2543.66	2530.40	1.0000	0.07507193	0.066158	16.70	12.63	0.00800000	37036.7	50.00	20.50	0.00400000	60617.6	0.05590049	60.00	49.00	11.00	0.000	2543.66	-17.30	0.00083893	-17.37	0.00000000	0.0000	22.32	0.00376653	22.20	0.00376653	21.4668	2112.69	0.00	2546.09	2546.09	0.07507193	16.60	13.14	0.00800000	36934.7	49.86	23.91	0.00800000	70850.1
SPACE3-1 ZONE COIL	COIL:HEATING:WATER	Zone Equipment	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE3-1 ATU	SPACE3-1	N/A	N/A	N/A	Yes	Yes	Yes	No	6198.123	6198.123	0.208927	0.00013694	137.946	1.0000	1.00000	1.00000	1012.2758	1004.8586	1.1347	unknown	unknown	-999.0	-999.0		4197.9300	999.8980	0.88934003	71.00	82.00	11.00	41067.26	15.1786	15.396359	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	unknown	unknown	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	6233.45	6198.12	1.0000	0.23707928	0.208927	16.70	12.63	0.00800000	37036.7	50.00	20.50	0.00400000	60617.6	0.13692599	60.00	49.00	11.00	0.000	6233.45	-17.30	0.00083893	-17.37	0.00000000	0.0000	22.32	0.00376874	22.20	0.00376874	21.4794	4878.99	0.00	6237.66	6237.66	0.23707928	16.60	13.14	0.00800000	36934.7	42.40	21.85	0.00800000	63245.2
SPACE4-1 ZONE COIL	COIL:HEATING:WATER	Zone Equipment	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE4-1 ATU	SPACE4-1	N/A	N/A	N/A	Yes	Yes	Yes	No	2900.125	2900.125	0.124714	0.00006407	60.797	1.0000	1.00000	1.00000	1012.2758	1004.8586	1.1347	unknown	unknown	-999.0	-999.0		4197.9300	999.8980	0.88934003	71.00	82.00	11.00	41067.26	7.1042	7.204015	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	unknown	unknown	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	2917.49	2900.13	1.0000	0.14151905	0.124714	16.70	12.63	0.00800000	37036.7	50.00	20.50	0.00400000	60617.6	0.06406819	60.00	49.00	11.00	0.000	2917.49	-17.30	0.00083893	-17.37	0.00000000	0.0000	22.32	0.00376653	22.20	0.00376653	21.4668	2112.69	0.00	2918.91	2918.91	0.14151905	16.60	13.14	0.00800000	36934.7	36.83	20.19	0.00800000	57560.3
SPACE5-1 ZONE COIL	COIL:HEATING:WATER	Zone Equipment	ZONEHVAC:AIRDISTRIBUTIONUNIT	SPACE5-1 ATU	SPACE5-1	N/A	N/A	N/A	Yes	Yes	Yes	No	4641.972	4641.972	0.121375	0.00010256	113.677	1.0000	1.00000	1.00000	1012.2758	1004.8586	1.1347	unknown	unknown	-999.0	-999.0		4197.9300	999.8980	0.88934003	71.00	82.00	11.00	41067.26	11.3626	11.530825	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	unknown	unknown	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	4666.29	4641.97	1.0000	0.13772940	0.121375	16.70	12.63	0.00800000	37036.7	50.00	20.50	0.00400000	60617.6	0.10254824	60.00	49.00	11.00	0.000	4666.29	-17.30	0.00083893	-17.37	0.00000000	0.0000	22.48	0.00348972	22.20	0.00348972	19.8981	3876.04	0.00	4670.75	4670.75	0.13772940	16.60	13.14	0.00800000	36934.7	49.86	23.91	0.00800000	70847.2
MAIN COOLING COIL 1	Coil:Cooling:Water	AirLoop	AirLoopHVAC	VAV SYS 1	SPACE1-1; SPACE2-1; SPACE3-1; SPACE4-1; SPACE5-1;	Non-Coincident	CoolingDesignCapacity	N/A	Yes	Yes	Yes	No	40439.257	-999.000	1.545497	0.00144440	-999.000	-999.0000	1.00000	1.00000	1025.7650	1004.8586	1.1347	SUPPLY FAN 1	Fan:VariableVolume	1.545497	1.75374571		4197.9300	999.8980	1.44424923	13.89	7.22	6.67	40439.26	100.0000	100.000000	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:00:00	CHICAGO_IL_USA ANNUAL COOLING 1% DESIGN CONDITIONS DB/MCWB	7/21 15:15:00	40439.26	27195.60	1.0000	1.75374571	1.545497	26.53	18.80	0.01125633	55367.7	12.06	10.76	0.00800000	32308.9	1.44424923	7.22	13.89	6.67	1324.712	39114.55	29.88	0.01459469	22.11	0.49088000	31.7619	24.98	0.00970247	23.90	0.00970247	49.4280	17732.00	0.00	42387.06	28165.59	1.75374571	26.53	19.46	0.01125633	55367.7	10.88	10.82	0.00803988	31198.3
MAIN HEATING COIL 1	Coil:Heating:Water	AirLoop	AirLoopHVAC	VAV SYS 1	SPACE1-1; SPACE2-1; SPACE3-1; SPACE4-1; SPACE5-1;	Non-Coincident	HeatingDesignCapacity	N/A	Yes	Yes	Yes	No	17975.118	17975.118	0.463649	0.00039714	241.473	-999.0000	1.00000	1.00000	1019.7116	1004.8586	1.1347	SUPPLY FAN 1	Fan:VariableVolume	1.545497	1.75374571		4197.9300	999.8980	0.88934003	71.00	82.00	11.00	41067.26	29.0013	44.650835	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 01:00:00	unknown	unknown	CHICAGO_IL_USA ANNUAL HEATING 99% DESIGN CONDITIONS DB	1/21 24:00:00	11910.04	13513.94	1.0000	0.52612371	0.463649	-8.49	-9.32	0.00147143	-4873.7	16.70	12.63	0.00800000	37036.7	0.39709775	60.00	49.00	11.00	0.000	11910.04	-17.30	0.00083893	-17.37	0.49088000	105.8732	22.36	0.00368629	22.20	0.00368629	21.0123	17999.41	0.00	11888.97	11888.97	0.52612371	16.60	5.13	0.00083893	18804.3	39.05	14.97	0.00083893	41401.6

Table of Contents
Report: System Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Economizer
	High Limit Shutoff Control	Minimum Outdoor Air [m3/s]	Maximum Outdoor Air [m3/s]	Return Air Temp Limit	Return Air Enthalpy Limit	Outdoor Air Temperature Limit [C]	Outdoor Air Enthalpy Limit [C]
OA CONTROLLER 1	FixedDryBulb	0.49	1.55	-

Demand Controlled Ventilation using Controller:MechanicalVentilation
	Controller:MechanicalVentilation Name	Outdoor Air Per Person [m3/s-person]	Outdoor Air Per Area [m3/s-m2]	Outdoor Air Per Zone [m3/s]	Outdoor Air ACH [ach]	Outdoor Air Method	Outdoor Air Schedule Name	Air Distribution Effectiveness in Cooling Mode	Air Distribution Effectiveness in Heating Mode	Air Distribution Effectiveness Schedule Name
None

Time Not Comfortable Based on Simple ASHRAE 55-2004
	Winter Clothes [hr]	Summer Clothes [hr]	Summer or Winter Clothes [hr]
SPACE1-1	1941.00	1622.50	1096.75
SPACE2-1	2290.75	1354.50	966.50
SPACE3-1	1764.50	1830.50	940.00
SPACE4-1	1356.00	1966.25	617.50
SPACE5-1	1238.00	2043.50	1237.25
PLENUM-1	0.00	0.00	0.00
Facility	2388.75	2498.00	1246.75

Aggregated over the RunPeriods for Weather
Time Setpoint Not Met
	During Heating [hr]	During Cooling [hr]	During Occupied Heating [hr]	During Occupied Cooling [hr]
SPACE1-1	0.00	54.75	0.00	54.75
SPACE2-1	0.00	248.50	0.00	218.25
SPACE3-1	0.00	18.00	0.00	0.00
SPACE4-1	0.00	102.50	0.00	0.00
SPACE5-1	0.50	0.00	0.00	0.00
PLENUM-1	0.00	0.00	0.00	0.00
Facility	0.50	423.75	0.00	273.00

Aggregated over the RunPeriods for Weather

Table of Contents
Report: Outdoor Air Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Average Outdoor Air During Occupied Hours
	Average Number of Occupants	Nominal Number of Occupants	Zone Volume [m3]	Mechanical Ventilation [ach]	Infiltration [ach]	AFN Infiltration [ach]	Simple Ventilation [ach]
SPACE1-1	9.50	11.00	239.25	1.358	0.016	0.000	0.000
SPACE2-1	4.32	5.00	103.31	1.866	0.016	0.000	0.000
SPACE3-1	9.50	11.00	239.25	1.999	0.016	0.000	0.000
SPACE4-1	4.32	5.00	103.31	2.757	0.016	0.000	0.000
SPACE5-1	17.27	20.00	447.68	0.830	0.016	0.000	0.000

Values shown for a single zone without multipliers
Minimum Outdoor Air During Occupied Hours
	Average Number of Occupants	Nominal Number of Occupants	Zone Volume [m3]	Mechanical Ventilation [ach]	Infiltration [ach]	AFN Infiltration [ach]	Simple Ventilation [ach]
SPACE1-1	9.50	11.00	239.25	0.026	0.000	0.000	0.000
SPACE2-1	4.32	5.00	103.31	0.027	0.000	0.000	0.000
SPACE3-1	9.50	11.00	239.25	0.040	0.000	0.000	0.000
SPACE4-1	4.32	5.00	103.31	0.055	0.000	0.000	0.000
SPACE5-1	17.27	20.00	447.68	0.012	0.000	0.000	0.000

Values shown for a single zone without multipliers

Table of Contents
Report: Object Count Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Surfaces by Class
	Total	Outdoors
Wall	24	8
Floor	10	5
Roof	6	1
Internal Mass	0	0
Building Detached Shading	0	0
Fixed Detached Shading	0	0
Window	6	6
Door	0	0
Glass Door	2	2
Shading	4	4
Overhang	0	0
Fin	0	0
Tubular Daylighting Device Dome	0	0
Tubular Daylighting Device Diffuser	0	0

HVAC
	Count
HVAC Air Loops	1
Conditioned Zones	6
Unconditioned Zones	0
Supply Plenums	0
Return Plenums	1

Input Fields
	Count
IDF Objects	0
Defaulted Fields	0
Fields with Defaults	0
Autosized Fields	0
Autosizable Fields	0
Autocalculated Fields	0
Autocalculatable Fields	0

Table of Contents
Report: Energy Meters
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Annual and Peak Values - Electricity
	Electricity Annual Value [kWh]	Electricity Minimum Value [W]	Timestamp of Minimum {TIMESTAMP}	Electricity Maximum Value [W]	Timestamp of Maximum {TIMESTAMP}
Electricity:Facility	51244.54	475.00	01-JAN-00:15	20112.67	22-MAR-11:00
Electricity:Building	35815.60	475.00	01-JAN-00:15	12000.00	01-JAN-10:15
Electricity:Zone:SPACE1-1	7564.26	100.32	01-JAN-00:15	2534.40	01-JAN-10:15
InteriorLights:Electricity	22566.39	375.00	01-JAN-00:15	7500.00	01-JAN-10:15
InteriorLights:Electricity:Zone:SPACE1-1	4766.02	79.20	01-JAN-00:15	1584.00	01-JAN-10:15
GeneralLights:InteriorLights:Electricity	22566.39	375.00	01-JAN-00:15	7500.00	01-JAN-10:15
Electricity:Zone:SPACE2-1	3266.38	43.32	01-JAN-00:15	1094.40	01-JAN-10:15
InteriorLights:Electricity:Zone:SPACE2-1	2058.06	34.20	01-JAN-00:15	684.00	01-JAN-10:15
Electricity:Zone:SPACE3-1	7564.26	100.32	01-JAN-00:15	2534.40	01-JAN-10:15
InteriorLights:Electricity:Zone:SPACE3-1	4766.02	79.20	01-JAN-00:15	1584.00	01-JAN-10:15
Electricity:Zone:SPACE4-1	3266.38	43.32	01-JAN-00:15	1094.40	01-JAN-10:15
InteriorLights:Electricity:Zone:SPACE4-1	2058.06	34.20	01-JAN-00:15	684.00	01-JAN-10:15
Electricity:Zone:SPACE5-1	14154.33	187.72	01-JAN-00:15	4742.40	01-JAN-10:15
InteriorLights:Electricity:Zone:SPACE5-1	8918.24	148.20	01-JAN-00:15	2964.00	01-JAN-10:15
InteriorEquipment:Electricity	13249.21	100.00	01-JAN-00:15	4500.00	01-JAN-09:15
InteriorEquipment:Electricity:Zone:SPACE1-1	2798.23	21.12	01-JAN-00:15	950.40	01-JAN-09:15
General:InteriorEquipment:Electricity	13249.21	100.00	01-JAN-00:15	4500.00	01-JAN-09:15
InteriorEquipment:Electricity:Zone:SPACE2-1	1208.33	9.12	01-JAN-00:15	410.40	01-JAN-09:15
InteriorEquipment:Electricity:Zone:SPACE3-1	2798.23	21.12	01-JAN-00:15	950.40	01-JAN-09:15
InteriorEquipment:Electricity:Zone:SPACE4-1	1208.33	9.12	01-JAN-00:15	410.40	01-JAN-09:15
InteriorEquipment:Electricity:Zone:SPACE5-1	5236.09	39.52	01-JAN-00:15	1778.40	01-JAN-09:15
ElectricityPurchased:Facility	41464.83	0.00	01-JAN-00:15	18829.72	22-MAR-11:00
ElectricityPurchased:Plant	41464.83	0.00	01-JAN-00:15	18829.72	22-MAR-11:00
Cogeneration:ElectricityPurchased	41464.83	0.00	01-JAN-00:15	18829.72	22-MAR-11:00
ElectricitySurplusSold:Facility	2205.26	0.00	01-JAN-06:15	1009.15	12-SEP-06:00
ElectricitySurplusSold:Plant	2205.26	0.00	01-JAN-06:15	1009.15	12-SEP-06:00
Cogeneration:ElectricitySurplusSold	2205.26	0.00	01-JAN-06:15	1009.15	12-SEP-06:00
ElectricityNet:Facility	39259.58	-1009.15	12-SEP-06:00	18829.72	22-MAR-11:00
ElectricityNet:Plant	39259.58	-1009.15	12-SEP-06:00	18829.72	22-MAR-11:00
Cogeneration:ElectricityNet	39259.58	-1009.15	12-SEP-06:00	18829.72	22-MAR-11:00
ElectricityProduced:Facility	11984.97	1245.79	20-MAY-15:00	1484.15	12-SEP-06:00
ElectricityProduced:Plant	11984.97	1245.79	20-MAY-15:00	1484.15	12-SEP-06:00
Cogeneration:ElectricityProduced	11984.97	1245.79	20-MAY-15:00	1484.15	12-SEP-06:00
Electricity:HVAC	2297.66	0.00	01-JAN-00:15	853.80	22-MAR-11:00
Fans:Electricity	2297.66	0.00	01-JAN-00:15	853.80	22-MAR-11:00
General:Fans:Electricity	2297.66	0.00	01-JAN-00:15	853.80	22-MAR-11:00
Electricity:Plant	13131.28	0.00	01-JAN-00:15	7690.89	22-FEB-16:00
Heating:Electricity	0.00	0.00	01-JAN-00:15	0.00	01-JAN-00:15
Boiler Parasitic:Heating:Electricity	0.00	0.00	01-JAN-00:15	0.00	01-JAN-00:15
Cooling:Electricity	12487.97	0.00	01-JAN-00:15	7499.95	22-FEB-16:00
General:Cooling:Electricity	12487.97	0.00	01-JAN-00:15	7499.95	22-FEB-16:00
Pumps:Electricity	643.31	0.00	01-JAN-00:15	310.56	01-APR-06:45
General:Pumps:Electricity	643.31	0.00	01-JAN-00:15	310.56	01-APR-06:45

Annual and Peak Values - Gas
	Gas Annual Value [kWh]	Gas Minimum Value [W]	Timestamp of Minimum {TIMESTAMP}	Gas Maximum Value [W]	Timestamp of Maximum {TIMESTAMP}
Gas:Facility	52397.99	4909.73	20-MAY-15:00	31443.99	12-SEP-06:15
Gas:Plant	52397.99	4909.73	20-MAY-15:00	31443.99	12-SEP-06:15
Cogeneration:Gas	45512.33	4909.73	20-MAY-15:00	5467.84	12-SEP-06:00
Heating:Gas	6885.66	0.00	01-JAN-00:15	25979.51	12-SEP-06:15
Boiler:Heating:Gas	6885.66	0.00	01-JAN-00:15	25979.51	12-SEP-06:15

Annual and Peak Values - Cooling
	Cooling Annual Value [kWh]	Cooling Minimum Value [W]	Timestamp of Minimum {TIMESTAMP}	Cooling Maximum Value [W]	Timestamp of Maximum {TIMESTAMP}
PlantLoopCoolingDemand:Facility	51332.36	0.00	01-JAN-00:15	28735.41	22-FEB-16:00
PlantLoopCoolingDemand:HVAC	51332.36	0.00	01-JAN-00:15	28735.41	22-FEB-16:00
CoolingCoils:PlantLoopCoolingDemand	51332.36	0.00	01-JAN-00:15	28735.41	22-FEB-16:00

Annual and Peak Values - Water
	Annual Value [m3]	Minimum Value [m3/s]	Timestamp of Minimum {TIMESTAMP}	Maximum Value [m3/s]	Timestamp of Maximum {TIMESTAMP}
Water:Facility	238.79	0.00	01-JAN-00:15	0.00	01-JAN-12:15
Water:Plant	238.79	0.00	01-JAN-00:15	0.00	01-JAN-12:15
WaterSystems:Water	238.79	0.00	01-JAN-00:15	0.00	01-JAN-12:15
Bathrooms:WaterSystems:Water	139.29	0.00	01-JAN-00:15	0.00	01-JAN-12:15
MainsWater:Facility	238.79	0.00	01-JAN-00:15	0.00	01-JAN-12:15
MainsWater:Plant	238.79	0.00	01-JAN-00:15	0.00	01-JAN-12:15
WaterSystems:MainsWater	238.79	0.00	01-JAN-00:15	0.00	01-JAN-12:15
Bathrooms:WaterSystems:MainsWater	139.29	0.00	01-JAN-00:15	0.00	01-JAN-12:15
Kitchen Sink:WaterSystems:Water	99.50	0.00	01-JAN-00:15	0.00	01-JAN-10:15
Kitchen Sink:WaterSystems:MainsWater	99.50	0.00	01-JAN-00:15	0.00	01-JAN-10:15

Annual and Peak Values - Other by Weight/Mass
	Annual Value [kg]	Minimum Value [kg/s]	Timestamp of Minimum {TIMESTAMP}	Maximum Value [kg/s]	Timestamp of Maximum {TIMESTAMP}
Carbon Equivalent:Facility	0.00	0.000	01-JAN-00:15	0.000	01-JAN-00:15
CarbonEquivalentEmissions:Carbon Equivalent	0.00	0.000	01-JAN-00:15	0.000	01-JAN-00:15

Annual and Peak Values - Other Volumetric
	Annual Value [m3]	Minimum Value [m3/s]	Timestamp of Minimum {TIMESTAMP}	Maximum Value [m3/s]	Timestamp of Maximum {TIMESTAMP}
None

Annual and Peak Values - Other Liquid/Gas
	Annual Value [L]	Minimum Value [L]	Timestamp of Minimum {TIMESTAMP}	Maximum Value [L]	Timestamp of Maximum {TIMESTAMP}
None

Annual and Peak Values - Other
	Annual Value [kWh]	Minimum Value [W]	Timestamp of Minimum {TIMESTAMP}	Maximum Value [W]	Timestamp of Maximum {TIMESTAMP}
EnergyTransfer:Facility	207294.83	0.00	01-JAN-20:15	105354.80	22-FEB-16:00
EnergyTransfer:Building	28814.40	0.00	01-JAN-20:15	14387.40	20-MAY-16:00
EnergyTransfer:Zone:PLENUM-1	3929.74	0.00	01-JAN-00:15	3723.81	07-NOV-15:45
Heating:EnergyTransfer	2654.78	0.00	01-JAN-11:45	11729.81	15-FEB-06:15
Heating:EnergyTransfer:Zone:PLENUM-1	843.51	0.00	01-JAN-00:15	1771.70	04-NOV-08:15
Cooling:EnergyTransfer	26159.62	0.00	01-JAN-00:15	14387.40	20-MAY-16:00
Cooling:EnergyTransfer:Zone:PLENUM-1	3086.22	0.00	01-JAN-00:15	3723.81	07-NOV-15:45
EnergyTransfer:Zone:SPACE1-1	5220.12	0.00	01-JAN-20:15	2917.33	04-JAN-17:30
Heating:EnergyTransfer:Zone:SPACE1-1	440.12	0.00	01-JAN-08:15	2634.63	15-FEB-06:15
Cooling:EnergyTransfer:Zone:SPACE1-1	4780.00	0.00	01-JAN-00:15	2917.33	04-JAN-17:30
EnergyTransfer:Zone:SPACE2-1	3020.15	0.00	01-JAN-20:15	1939.39	02-APR-10:30
Heating:EnergyTransfer:Zone:SPACE2-1	140.93	0.00	01-JAN-08:15	1258.21	12-SEP-06:15
Cooling:EnergyTransfer:Zone:SPACE2-1	2879.21	0.00	01-JAN-00:15	1939.39	02-APR-10:30
EnergyTransfer:Zone:SPACE3-1	6803.30	0.00	01-JAN-20:15	5496.50	12-JUL-10:30
Heating:EnergyTransfer:Zone:SPACE3-1	330.39	0.00	01-JAN-08:15	2589.54	15-FEB-06:15
Cooling:EnergyTransfer:Zone:SPACE3-1	6472.91	0.00	01-JAN-00:15	5496.50	12-JUL-10:30
EnergyTransfer:Zone:SPACE4-1	3683.25	0.00	01-JAN-20:15	2917.93	20-MAY-16:30
Heating:EnergyTransfer:Zone:SPACE4-1	188.03	0.00	01-JAN-08:15	1243.65	12-SEP-06:15
Cooling:EnergyTransfer:Zone:SPACE4-1	3495.23	0.00	01-JAN-00:15	2917.93	20-MAY-16:30
EnergyTransfer:Zone:SPACE5-1	6157.84	0.00	01-JAN-20:15	3344.71	15-FEB-06:15
Heating:EnergyTransfer:Zone:SPACE5-1	711.79	0.00	01-JAN-08:15	3344.71	15-FEB-06:15
Cooling:EnergyTransfer:Zone:SPACE5-1	5446.05	0.00	01-JAN-00:15	2662.94	03-SEP-15:00
DistrictHeating:Facility	9473.14	0.00	01-JAN-00:15	4747.65	01-JAN-12:15
DistrictHeating:Plant	9473.14	0.00	01-JAN-00:15	4747.65	01-JAN-12:15
WaterSystems:DistrictHeating	9473.14	0.00	01-JAN-00:15	4747.65	01-JAN-12:15
Bathrooms:WaterSystems:DistrictHeating	4852.10	0.00	01-JAN-00:15	1582.55	01-JAN-12:15
Kitchen Sink:WaterSystems:DistrictHeating	4621.05	0.00	01-JAN-00:15	3165.10	19-MAY-14:00
EnergyTransfer:HVAC	56842.19	0.00	01-JAN-00:15	33328.23	11-APR-06:15
HeatingCoils:EnergyTransfer	5509.83	0.00	01-JAN-00:15	16757.83	16-JUL-06:15
PlantLoopHeatingDemand:Facility	5509.83	0.00	01-JAN-00:15	16757.83	16-JUL-06:15
PlantLoopHeatingDemand:HVAC	5509.83	0.00	01-JAN-00:15	16757.83	16-JUL-06:15
HeatingCoils:PlantLoopHeatingDemand	5509.83	0.00	01-JAN-00:15	16757.83	16-JUL-06:15
CoolingCoils:EnergyTransfer	51332.36	0.00	01-JAN-00:15	28735.41	22-FEB-16:00
EnergyTransfer:Plant	121638.23	0.00	01-JAN-00:15	65180.45	22-FEB-16:00
Boilers:EnergyTransfer	5508.53	0.00	01-JAN-00:15	20783.61	12-SEP-06:15
Chillers:EnergyTransfer	51820.87	0.00	01-JAN-00:15	28868.59	11-APR-16:00
HeatRejection:EnergyTransfer	64308.84	0.00	01-JAN-00:15	36340.20	22-FEB-16:00

Table of Contents
Report: Sensible Heat Gain Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Annual Building Sensible Heat Gain Components
	HVAC Zone Eq & Other Sensible Air Heating [kWh]	HVAC Zone Eq & Other Sensible Air Cooling [kWh]	HVAC Terminal Unit Sensible Air Heating [kWh]	HVAC Terminal Unit Sensible Air Cooling [kWh]	HVAC Input Heated Surface Heating [kWh]	HVAC Input Cooled Surface Cooling [kWh]	People Sensible Heat Addition [kWh]	Lights Sensible Heat Addition [kWh]	Equipment Sensible Heat Addition [kWh]	Window Heat Addition [kWh]	Interzone Air Transfer Heat Addition [kWh]	Infiltration Heat Addition [kWh]	Opaque Surface Conduction and Other Heat Addition [kWh]	Equipment Sensible Heat Removal [kWh]	Window Heat Removal [kWh]	Interzone Air Transfer Heat Removal [kWh]	Infiltration Heat Removal [kWh]	Opaque Surface Conduction and Other Heat Removal [kWh]
SPACE1-1	0.000	0.000	346.979	-4780.19	0.000	0.000	1930.695	4766.022	2798.233	6206.843	0.000	14.811	0.000	0.000	-327.79	0.000	-3.91	-10951.70
SPACE2-1	0.000	0.000	100.730	-2879.34	0.000	0.000	870.140	2058.055	1208.328	5327.089	0.000	5.901	0.000	0.000	-135.90	0.000	-2.59	-6552.41
SPACE3-1	0.000	0.000	237.230	-6473.09	0.000	0.000	1981.608	4766.022	2798.233	10369.327	0.000	16.076	0.000	0.000	-357.92	0.000	-3.65	-13333.84
SPACE4-1	0.000	0.000	147.788	-3495.29	0.000	0.000	919.983	2058.055	1208.328	5530.026	0.000	6.964	0.000	0.000	-150.28	0.000	-1.71	-6223.87
SPACE5-1	0.000	0.000	537.394	-5446.37	0.000	0.000	3498.552	8918.239	5236.088	0.000	0.000	35.779	0.000	0.000	0.000	0.000	-7.82	-12771.87
PLENUM-1	843.566	-3086.19	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000	0.000	2242.623	0.000	0.000	0.000	0.000	-0.21
Total Facility	843.566	-3086.19	1370.120	-23074.28	0.000	0.000	9200.978	22566.393	13249.211	27433.285	0.000	79.531	2242.623	0.000	-971.88	0.000	-19.67	-49833.90

Peak Cooling Sensible Heat Gain Components
	Time of Peak {TIMESTAMP}	HVAC Zone Eq & Other Sensible Air Heating [W]	HVAC Zone Eq & Other Sensible Air Cooling [W]	HVAC Terminal Unit Sensible Air Heating [W]	HVAC Terminal Unit Sensible Air Cooling [W]	HVAC Input Heated Surface Heating [W]	HVAC Input Cooled Surface Cooling [W]	People Sensible Heat Addition [W]	Lights Sensible Heat Addition [W]	Equipment Sensible Heat Addition [W]	Window Heat Addition [W]	Interzone Air Transfer Heat Addition [W]	Infiltration Heat Addition [W]	Opaque Surface Conduction and Other Heat Addition [W]	Equipment Sensible Heat Removal [W]	Window Heat Removal [W]	Interzone Air Transfer Heat Removal [W]	Infiltration Heat Removal [W]	Opaque Surface Conduction and Other Heat Removal [W]
SPACE1-1	04-JAN-17:30	0.00	0.00	0.00	-2917.40	0.00	0.00	691.59	1584.00	528.00	7724.01	0.00	9.33	0.00	0.00	-0.00	0.00	0.00	-7619.52
SPACE2-1	02-APR-10:15	0.00	0.00	0.00	-1939.83	0.00	0.00	345.50	684.00	410.40	3240.12	0.00	0.00	0.00	0.00	-0.00	0.00	0.00	-2740.19
SPACE3-1	12-JUL-10:30	0.00	0.00	0.00	-5496.40	0.00	0.00	766.44	1584.00	950.40	10323.39	0.00	0.00	0.00	0.00	-0.00	0.00	0.00	-8127.83
SPACE4-1	20-MAY-16:30	0.00	0.00	0.00	-2917.91	0.00	0.00	348.38	684.00	228.00	5725.20	0.00	0.00	0.00	0.00	-0.00	0.00	0.00	-4067.67
SPACE5-1	03-SEP-15:00	0.00	0.00	0.00	-2663.09	0.00	0.00	1393.56	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	-0.00	0.00	0.00	-3275.27
PLENUM-1	07-NOV-15:45	0.00	-3724.22	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	3724.22	0.00	-0.00	0.00	0.00	0.00
Total Facility	20-MAY-16:00	0.00	-3242.27	0.00	-11145.25	0.00	0.00	3638.97	7500.00	3500.00	9434.80	0.00	0.00	0.00	0.00	0.00	0.00	0.00	-9686.26

Peak Heating Sensible Heat Gain Components
	Time of Peak {TIMESTAMP}	HVAC Zone Eq & Other Sensible Air Heating [W]	HVAC Zone Eq & Other Sensible Air Cooling [W]	HVAC Terminal Unit Sensible Air Heating [W]	HVAC Terminal Unit Sensible Air Cooling [W]	HVAC Input Heated Surface Heating [W]	HVAC Input Cooled Surface Cooling [W]	People Sensible Heat Addition [W]	Lights Sensible Heat Addition [W]	Equipment Sensible Heat Addition [W]	Window Heat Addition [W]	Interzone Air Transfer Heat Addition [W]	Infiltration Heat Addition [W]	Opaque Surface Conduction and Other Heat Addition [W]	Equipment Sensible Heat Removal [W]	Window Heat Removal [W]	Interzone Air Transfer Heat Removal [W]	Infiltration Heat Removal [W]	Opaque Surface Conduction and Other Heat Removal [W]
SPACE1-1	04-NOV-06:02	0.00	0.00	5629.53	-0.00	0.00	0.00	0.00	79.20	21.12	0.00	0.00	0.00	0.00	0.00	-101.30	0.00	-36.72	-5591.82
SPACE2-1	16-JAN-06:02	0.00	0.00	2837.74	-0.00	0.00	0.00	0.00	34.20	9.12	0.00	0.00	0.00	0.00	0.00	-72.35	0.00	-0.50	-2808.22
SPACE3-1	16-JAN-06:02	0.00	0.00	4850.10	-0.00	0.00	0.00	0.00	79.20	21.12	0.00	0.00	0.00	0.00	0.00	-192.27	0.00	-1.03	-4757.13
SPACE4-1	15-NOV-06:02	0.00	0.00	2193.66	-0.00	0.00	0.00	0.00	34.20	9.12	0.00	0.00	0.00	0.00	0.00	-13.72	0.00	-2.12	-2221.14
SPACE5-1	16-JAN-06:02	0.00	0.00	5510.23	-0.00	0.00	0.00	0.00	148.20	39.52	0.00	0.00	0.00	0.00	0.00	-0.00	0.00	-1.96	-5695.99
PLENUM-1	04-NOV-08:08	1819.93	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	-0.00	0.00	0.00	-1819.93
Total Facility	16-JAN-06:02	-284.93	0.00	21010.04	0.00	0.00	0.00	0.00	375.00	100.00	0.00	0.00	0.00	0.00	0.00	-519.36	0.00	-5.03	-20675.72

Table of Contents
Report: Standard 62.1 Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
System Ventilation Requirements for Cooling
	Sum of Zone Primary Air Flow - Vpz-sum [m3/s]	System Population - Ps	Sum of Zone Population - Pz-sum	Occupant Diversity - D	Uncorrected Outdoor Air Intake Airflow - Vou [m3/s]	System Primary Airflow - Vps [m3/s]	Average Outdoor Air Fraction - Xs	System Ventilation Efficiency - Ev	Outdoor Air Intake Flow - Vot [m3/s]	Percent Outdoor Air - %OA	Environment Name of Peak System Population - Ps	Date and Time of Last Peak System Population - Ps
VAV SYS 1	1.5455	0.0000	52.0000	1.0000	0.4909	1.5455	0.3176	1.0000	0.4909	0.3176

System Ventilation Requirements for Heating
	Sum of Zone Primary Air Flow - Vpz-sum [m3/s]	System Population - Ps	Sum of Zone Population - Pz-sum	Occupant Diversity - D	Uncorrected Outdoor Air Intake Airflow - Vou [m3/s]	System Primary Airflow - Vps [m3/s]	Average Outdoor Air Fraction - Xs	System Ventilation Efficiency - Ev	Outdoor Air Intake Flow Vot [m3/s]	Percent Outdoor Air - %OA	Environment Name of Peak System Population - Ps	Date and Time of Last Peak System Population - Ps
VAV SYS 1	0.9887	0.0000	52.0000	1.0000	0.4909	0.6182	1.0000	1.0000	0.4909	0.7940

Zone Ventilation Parameters
	AirLoop Name	People Outdoor Air Rate - Rp [m3/s-person]	Zone Population - Pz	Area Outdoor Air Rate - Ra [m3/s-m2]	Zone Floor Area - Az [m2]	Breathing Zone Outdoor Airflow - Vbz [m3/s]	Cooling Zone Air Distribution Effectiveness - Ez-clg	Cooling Zone Outdoor Airflow - Voz-clg [m3/s]	Heating Zone Air Distribution Effectiveness - Ez-htg	Heating Zone Outdoor Airflow - Voz-htg [m3/s]
SPACE1-1	VAV SYS 1	0.009440	11.0000	0.000000	99.16	0.1038	1.0000	0.1038	1.000	0.1038
SPACE2-1	VAV SYS 1	0.009440	5.0000	0.000000	42.73	0.0472	1.0000	0.0472	1.000	0.0472
SPACE3-1	VAV SYS 1	0.009440	11.0000	0.000000	96.48	0.1038	1.0000	0.1038	1.000	0.1038
SPACE4-1	VAV SYS 1	0.009440	5.0000	0.000000	42.73	0.0472	1.0000	0.0472	1.000	0.0472
SPACE5-1	VAV SYS 1	0.009440	20.0000	0.000000	182.49	0.1888	1.0000	0.1888	1.000	0.1888

System Ventilation Parameters
	People Outdoor Air Rate - Rp [m3/s-person]	Sum of Zone Population - Pz-sum	Area Outdoor Air Rate - Ra [m3/s-m2]	Sum of Zone Floor Area - Az-sum [m2]	Breathing Zone Outdoor Airflow - Vbz [m3/s]	Cooling Zone Outdoor Airflow - Voz-clg [m3/s]	Heating Zone Outdoor Airflow - Voz-htg [m3/s]
VAV SYS 1	0.009440	52.00	0.000000	463.6000	0.4909	0.4909	0.4909

Zone Ventilation Calculations for Cooling Design
	AirLoop Name	Box Type	Zone Primary Airflow - Vpz [m3/s]	Zone Discharge Airflow - Vdz [m3/s]	Minimum Zone Primary Airflow - Vpz-min [m3/s]	Zone Outdoor Airflow Cooling - Voz-clg [m3/s]	Primary Outdoor Air Fraction - Zpz	Primary Air Fraction - Ep	Secondary Recirculation Fraction- Er	Supply Air Fraction- Fa	Mixed Air Fraction - Fb	Outdoor Air Fraction - Fc	Zone Ventilation Efficiency - Evz
SPACE1-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2652	0.2652	0.1061	0.1038	0.0000	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE2-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.1510	0.1510	0.0604	0.0472	0.0000	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE3-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.5223	0.5223	0.2089	0.1038	0.0000	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE4-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.3118	0.3118	0.1247	0.0472	0.0000	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE5-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2952	0.2952	0.1181	0.1888	0.0000	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000

System Ventilation Calculations for Cooling Design
	Sum of Zone Primary Airflow - Vpz-sum [m3/s]	System Primary Airflow - Vps [m3/s]	Sum of Zone Discharge Airflow - Vdz-sum [m3/s]	Sum of Min Zone Primary Airflow - Vpz-min [m3/s]	Zone Outdoor Airflow Cooling - Voz-clg [m3/s]	Zone Ventilation Efficiency - Evz-min
VAV SYS 1	1.5455	1.5455	1.5455	0.6182	0.4909	1.0000

Zone Ventilation Calculations for Heating Design
	AirLoop Name	Box Type	Zone Primary Airflow - Vpz [m3/s]	Zone Discharge Airflow - Vdz [m3/s]	Minimum Zone Primary Airflow - Vpz-min [m3/s]	Zone Outdoor Airflow Heating - Voz-htg [m3/s]	Primary Outdoor Air Fraction - Zpz	Primary Air Fraction - Ep	Secondary Recirculation Fraction- Er	Supply Air Fraction- Fa	Mixed Air Fraction - Fb	Outdoor Air Fraction - Fc	Zone Ventilation Efficiency - Evz
SPACE1-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2015	0.2015	0.1061	0.1038	0.6607	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE2-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.1416	0.1416	0.0604	0.0472	0.7134	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE3-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2089	0.2089	0.2089	0.1038	0.6797	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE4-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.1416	0.1416	0.1247	0.0472	0.7134	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000
SPACE5-1	VAV SYS 1	AIRTERMINAL:SINGLEDUCT:VAV:REHEAT	0.2952	0.2952	0.1181	0.1888	1.0000	1.0000	0.0000	0.0000	0.0000	0.0000	1.0000

System Ventilation Calculations for Heating Design
	Sum of Zone Primary Airflow - Vpz-sum [m3/s]	System Primary Airflow - Vps [m3/s]	Sum of Zone Discharge Airflow - Vdz-sum [m3/s]	Sum of Min Zone Primary Airflow - Vpz-min [m3/s]	Zone Outdoor Airflow Heating - Voz-htg [m3/s]	Zone Ventilation Efficiency - Evz-min
VAV SYS 1	0.9887	0.6182	0.6182	0.6182	0.4909	1.0000

Table of Contents
Report: LEED Summary
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Sec1.1A-General Information
	Data
Weather File	RUNPERIOD 1 ** TENA - - MN7 WMO#=999
Total gross floor area [m2]	927.20
Principal Heating Source	Natural Gas

EAp2-1. Space Usage Type
	Space Area [m2]	Regularly Occupied Area [m2]	Unconditioned Area [m2]	Typical Hours/Week in Operation [hr/wk]
SPACE1-1	99.16	99.16	0.00	55.06
SPACE2-1	42.73	42.73	0.00	55.06
SPACE3-1	96.48	96.48	0.00	55.06
SPACE4-1	42.73	42.73	0.00	55.06
SPACE5-1	182.49	182.49	0.00	55.06
PLENUM-1	463.60	463.60	0.00	0.00
Totals	927.20	927.20	0.00

EAp2-2. Advisory Messages
	Data
Number of hours heating loads not met	0.00
Number of hours cooling loads not met	273.00
Number of hours not met	273.00

EAp2-3. Energy Type Summary
	Utility Rate	Virtual Rate [$/unit energy]	Units of Energy	Units of Demand
Electricity	EXAMPLED EXAMPLEI-SELL	0.053	kWh	kW
Natural Gas	EXAMPLEA-GAS	0.601	Therm	Therm/Hr
Other	WATER TARIFF	7.000		/Hr

EAp2-4/5. Performance Rating Method Compliance
	Electric Energy Use [kWh]	Electric Demand [W]	Natural Gas Energy Use [kWh]	Natural Gas Demand [W]	Additional Fuel Use [kWh]	Additional Fuel Demand [W]	District Cooling Use [kWh]	District Cooling Demand [W]	District Heating Use [kWh]	District Heating Demand [W]
Heating -- Boiler	0.00	0.00	6885.66	25979.51	0.00	0.00	0.00	0.00	0.00	0.00
Heating -- Boiler Parasitic	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Cooling -- General	12487.97	7499.95	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Interior Lighting -- GeneralLights	22566.39	7500.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Exterior Lighting -- Not Subdivided	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Interior Equipment -- General	13249.21	4500.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Exterior Equipment -- Not Subdivided	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Fans -- General	2297.66	853.80	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Pumps -- General	643.31	310.56	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Heat Rejection -- Not Subdivided	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Humidification -- Not Subdivided	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Heat Recovery -- Not Subdivided	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Water Systems -- Bathrooms	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	4852.10	1582.55
Water Systems -- Kitchen Sink	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	4621.05	3165.10
Refrigeration -- Not Subdivided	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Generators -- Not Subdivided	0.00	0.00	45512.33	5467.84	0.00	0.00	0.00	0.00	0.00	0.00

EAp2-6. Energy Use Summary
	Process Subtotal [kWh]	Total Energy Use [kWh]
Electricity	13249.21	51244.54
Natural Gas	0.00	52397.99
Total	13249.21	113115.68
Additional	0.00	9473.14

EAp2-7. Energy Cost Summary
	Process Subtotal [$]	Total Energy Cost [$]
Electricity	570.73	2207.45
Natural Gas	0.00	1073.95
Other		1671.53
Total	570.73	4952.93
Additional	0.00

Process energy cost based on ratio of process to total energy.
L-1. Renewable Energy Source Summary
	Rated Capacity [kW]	Annual Energy Generated [kWh]
Photovoltaic	0.00	0.00
Wind	0.00	0.00

EAp2-17a. Energy Use Intensity - Electricity
	Electricty [kWh/m2]
Interior Lighting (All)	24.34
Space Heating	0.00
Space Cooling	13.47
Fans (All)	2.48
Service Water Heating	0.00
Receptacle Equipment	14.29
Miscellaneous (All)	55.27
Subtotal	55.27

EAp2-17b. Energy Use Intensity - Natural Gas
	Natural Gas [kWh/m2]
Space Heating	7.43
Service Water Heating	0.00
Miscellaneous (All)	56.51
Subtotal	56.51

EAp2-17c. Energy Use Intensity - Additional
	Additional [kWh/m2]
Subtotal	0.00
Miscellaneous	0.00

EAp2-18. End Use Percentage
	Percent [%]
Interior Lighting (All)	19.95
Space Heating	6.09
Space Cooling	11.04
Fans (All)	2.03
Service Water Heating	8.37
Receptacle Equipment	11.71
Miscellaneous	40.80

Schedules-Equivalent Full Load Hours (Schedule Type=Fraction)
	Equivalent Full Load Hours of Operation Per Year [hr]	Hours > 1% [hr]
OCCUPY-1	2479.	2871.
LIGHTS-1	3009.	8760.
EQUIP-1	2650.	8760.
INFIL-SCH	3624.	3624.
SHADETRANSSCH	0.	0.
MIN OA SCHED	3245.	8760.
FANAVAILSCHED	6202.	6202.
COOLINGCOILAVAILSCHED	3654.	3654.
COOLINGPUMPAVAILSCHED	8760.	8760.
REHEATCOILAVAILSCHED	3654.	3654.
PLANTONSCHED	8760.	8760.

Schedules-SetPoints (Schedule Type=Temperature)
	First Object Used	Month Assumed	11am First Wednesday [C]	Days with Same 11am Value	11pm First Wednesday [C]	Days with Same 11pm Value
HTG-SETP-SCH	HEATINGSETPOINT	July	22.20	365	16.70	365
PLENUMHTG-SETP-SCH	PLENUMHEATINGSETPOINT	July	12.80	365	12.80	365
CLG-SETP-SCH	COOLINGSETPOINT	January	23.90	365	29.40	365
PLENUMCLG-SETP-SCH	PLENUMCOOLINGSETPOINT	January	40.00	365	40.00	365

Table of Contents
Report: ZONE COOLING SUMMARY
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY [kWh]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {Maximum}[W]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]
January	261.27	3648.48	04-JAN-16:00	31.00	21.30	0.00	0.00	01-JAN-00:15	25.55	23.31
February	252.65	3300.76	08-FEB-16:00	28.10	19.38	0.00	0.00	01-FEB-00:15	23.22	18.57
March	257.41	3516.08	05-MAR-16:00	28.30	21.19	0.00	0.00	01-MAR-00:15	24.35	22.30
April	289.80	3047.85	08-APR-16:00	30.60	20.97	0.00	0.00	01-APR-00:15	24.55	20.48
May	245.28	3242.25	20-MAY-16:00	31.50	20.62	0.00	0.00	01-MAY-00:15	21.03	18.69
June	237.99	2840.03	25-JUN-16:00	29.20	19.47	0.00	0.00	01-JUN-00:15	22.65	20.45
July	233.73	2392.95	17-JUL-16:00	26.50	18.81	0.00	0.00	01-JUL-00:15	21.40	19.20
August	237.60	3154.90	30-AUG-16:00	28.60	18.61	0.00	0.00	01-AUG-00:15	20.90	19.84
September	266.33	2974.70	03-SEP-16:00	28.30	20.09	0.00	0.00	01-SEP-00:15	21.65	19.88
October	296.57	3324.24	18-OCT-16:00	28.60	20.90	0.00	0.00	01-OCT-00:15	20.52	18.15
November	252.84	3723.81	07-NOV-15:45	28.60	17.90	0.00	0.00	01-NOV-00:15	18.32	15.04
December	254.75	3273.56	20-DEC-15:45	30.47	19.84	0.00	0.00	01-DEC-00:15	21.05	17.81

Annual Sum or Average	3086.22					0.00
Minimum of Months	233.73	2392.95		26.50	17.90	0.00	0.00		18.32	15.04
Maximum of Months	296.57	3723.81		31.50	21.30	0.00	0.00		25.55	23.31

Table of Contents
Report: ZONE COOLING SUMMARY
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY [kWh]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {Maximum}[W]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]
January	410.48	2917.33	04-JAN-17:30	29.45	20.76	112.39	604.09	04-JAN-17:45	29.13	20.83
February	361.53	2578.71	08-FEB-17:15	27.12	19.28	97.53	545.94	08-FEB-17:30	26.85	19.19
March	369.35	2434.18	05-MAR-17:30	27.00	20.26	102.53	523.23	18-MAR-14:15	27.25	22.97
April	416.17	2455.18	10-APR-15:00	30.60	21.77	106.23	523.23	24-APR-14:15	27.92	21.05
May	409.88	2418.36	02-MAY-14:45	30.35	20.98	110.40	523.22	07-MAY-17:45	26.75	18.87
June	360.25	2243.38	25-JUN-15:00	29.40	19.63	96.47	523.23	13-JUN-14:30	26.80	19.65
July	409.97	2292.55	29-JUL-14:30	28.10	21.89	110.73	523.23	24-JUL-14:30	26.20	19.99
August	405.66	2434.15	19-AUG-14:45	29.55	19.79	106.10	523.23	14-AUG-14:15	28.47	18.91
September	409.56	2525.29	19-SEP-17:30	24.60	18.78	101.22	523.23	19-SEP-14:15	26.45	18.72
October	430.82	2542.73	30-OCT-16:45	26.38	18.44	112.42	539.88	30-OCT-16:00	26.20	18.39
November	383.27	2664.85	15-NOV-16:45	27.60	18.89	102.81	560.59	15-NOV-16:00	27.30	18.74
December	413.06	2883.33	20-DEC-17:30	28.80	18.76	108.14	598.27	20-DEC-17:45	28.45	18.59

Annual Sum or Average	4779.99					1266.97
Minimum of Months	360.25	2243.38		24.60	18.44	96.47	523.22		26.20	18.39
Maximum of Months	430.82	2917.33		30.60	21.89	112.42	604.09		29.13	22.97

Table of Contents
Report: ZONE COOLING SUMMARY
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY [kWh]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {Maximum}[W]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]
January	245.66	1883.41	23-JAN-10:30	27.85	20.18	52.00	306.65	23-JAN-10:45	28.33	20.26
February	222.33	1754.49	22-FEB-10:30	29.55	22.51	45.05	287.76	22-FEB-10:45	30.02	22.60
March	228.89	1747.51	18-MAR-10:15	28.33	23.30	47.39	286.83	18-MAR-10:30	28.55	23.38
April	249.03	1939.82	02-APR-10:15	24.95	19.12	48.54	241.56	02-APR-10:30	25.40	19.15
May	231.21	1500.02	20-MAY-09:45	26.65	20.06	50.12	237.83	20-MAY-09:15	25.75	20.11
June	206.88	1316.99	12-JUN-10:15	23.43	17.04	44.12	237.83	13-JUN-14:30	26.80	19.65
July	238.11	1473.00	12-JUL-10:30	25.45	19.59	50.61	237.83	22-JUL-09:30	23.25	17.25
August	238.21	1774.01	30-AUG-09:45	23.17	16.88	48.50	237.83	14-AUG-14:15	28.47	18.91
September	250.87	1935.05	30-SEP-09:45	22.90	17.29	46.33	240.93	30-SEP-09:00	23.40	17.06
October	275.15	1726.78	11-OCT-09:45	24.45	19.01	52.49	283.90	11-OCT-09:00	24.90	18.81
November	247.79	1760.64	07-NOV-09:53	23.40	16.12	48.12	289.47	07-NOV-09:00	23.40	16.12
December	245.08	1847.53	10-DEC-10:15	27.63	18.80	50.08	301.41	10-DEC-10:30	28.05	18.95

Annual Sum or Average	2879.21					583.34
Minimum of Months	206.88	1316.99		22.90	16.12	44.12	237.83		23.25	16.12
Maximum of Months	275.15	1939.82		29.55	23.30	52.49	306.65		30.02	23.38

Table of Contents
Report: ZONE COOLING SUMMARY
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY [kWh]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {Maximum}[W]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]
January	472.72	2613.97	23-JAN-14:30	29.50	20.30	108.02	523.23	16-JAN-14:15	27.60	19.02
February	432.74	2674.54	22-FEB-14:15	30.60	22.80	94.90	523.23	04-FEB-14:15	25.30	19.22
March	479.65	3612.58	27-MAR-10:30	28.50	23.66	100.31	523.23	01-MAR-14:15	26.75	23.72
April	606.29	4294.09	22-APR-10:30	26.75	20.88	100.88	523.22	22-APR-10:30	26.75	20.88
May	632.88	4778.51	21-MAY-10:30	27.30	19.91	103.99	523.22	21-MAY-09:30	25.80	20.07
June	611.76	5213.34	12-JUN-10:30	23.75	17.27	93.13	523.23	26-JUN-14:15	26.75	20.27
July	675.97	5496.50	12-JUL-10:30	25.45	19.59	106.14	523.23	17-JUL-14:15	26.45	18.81
August	618.70	5267.66	01-AUG-10:30	24.60	20.01	100.90	523.22	30-AUG-10:30	24.60	17.26
September	555.98	3790.89	09-SEP-10:30	23.90	19.46	95.54	523.22	09-SEP-10:30	23.90	19.46
October	506.00	2551.38	03-OCT-10:45	22.50	16.49	109.91	523.24	28-OCT-14:30	23.40	18.27
November	433.10	2494.27	11-NOV-14:15	29.55	21.31	99.10	523.25	15-NOV-15:15	28.80	19.11
December	447.13	2453.15	10-DEC-14:15	28.25	18.77	103.22	523.24	13-DEC-14:30	29.10	19.29

Annual Sum or Average	6472.91					1216.06
Minimum of Months	432.74	2453.15		22.50	16.49	93.13	523.22		23.40	17.26
Maximum of Months	675.97	5496.50		30.60	23.66	109.91	523.25		29.10	23.72

Table of Contents
Report: ZONE COOLING SUMMARY
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY [kWh]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {Maximum}[W]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]
January	261.01	1878.98	25-JAN-17:00	27.20	20.08	47.35	237.83	30-JAN-17:00	28.10	19.75
February	230.82	1743.88	08-FEB-16:30	27.75	19.38	41.65	237.83	08-FEB-17:00	26.30	19.00
March	245.48	2299.66	05-MAR-16:30	27.95	20.72	43.74	237.83	12-MAR-17:00	25.80	21.77
April	327.35	2664.64	15-APR-16:30	29.70	20.56	44.13	237.82	23-APR-17:00	27.10	21.02
May	329.32	2917.93	20-MAY-16:30	31.10	20.64	45.77	237.83	07-MAY-16:45	27.70	18.53
June	311.78	2808.97	25-JUN-16:30	28.80	19.55	40.48	237.82	06-JUN-17:00	24.20	18.05
July	337.70	2691.20	22-JUL-16:30	28.40	20.82	46.18	237.82	01-JUL-16:30	25.75	18.95
August	336.79	2800.06	20-AUG-16:30	28.75	20.09	44.30	237.82	08-AUG-17:00	24.60	18.71
September	319.43	2669.98	05-SEP-16:30	28.40	20.46	42.52	237.82	27-SEP-17:00	24.40	19.15
October	295.45	2445.14	07-OCT-16:00	26.80	19.05	48.33	237.84	04-OCT-17:15	25.45	17.26
November	247.72	2086.90	13-NOV-16:00	28.20	18.29	43.54	237.84	15-NOV-16:15	28.20	19.17
December	252.37	1741.88	17-DEC-16:45	29.25	19.36	45.51	237.84	12-DEC-17:00	27.90	18.46

Annual Sum or Average	3495.23					533.50
Minimum of Months	230.82	1741.88		26.80	18.29	40.48	237.82		24.20	17.26
Maximum of Months	337.70	2917.93		31.10	20.82	48.33	237.84		28.20	21.77

Table of Contents
Report: ZONE COOLING SUMMARY
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY [kWh]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {Maximum}[W]	ZONE TOTAL INTERNAL LATENT GAIN ENERGY {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]
January	434.40	2382.76	10-JAN-15:00	28.60	20.71	204.09	951.35	07-JAN-09:00	24.60	18.23
February	383.79	2409.97	27-FEB-15:00	31.00	23.28	177.49	951.35	08-FEB-09:00	23.40	17.98
March	412.39	2432.63	21-MAR-15:00	29.10	22.58	186.61	951.35	11-MAR-09:00	23.60	19.34
April	465.80	2497.49	08-APR-15:00	30.80	20.93	194.53	951.33	22-APR-09:00	26.00	20.71
May	481.92	2573.70	20-MAY-15:00	31.70	20.33	203.38	951.32	01-MAY-09:00	25.30	21.61
June	440.10	2567.76	25-JUN-15:00	29.40	19.63	177.10	951.33	06-JUN-09:00	22.70	18.53
July	505.07	2561.16	17-JUL-15:00	26.60	19.07	203.74	951.32	29-JUL-09:00	24.20	20.17
August	494.68	2647.10	19-AUG-15:00	29.60	19.78	195.04	951.32	30-AUG-09:00	23.70	17.00
September	475.44	2662.94	03-SEP-15:00	28.50	20.07	186.22	951.33	23-SEP-09:00	22.40	17.83
October	486.97	2527.89	11-OCT-15:00	29.70	20.85	204.88	951.34	29-OCT-09:00	22.30	19.92
November	433.04	2549.62	11-NOV-15:00	29.70	21.43	186.84	951.37	12-NOV-17:15	23.30	18.52
December	432.44	2543.78	12-DEC-15:00	30.70	18.92	195.46	951.35	11-DEC-09:00	23.70	18.24

Annual Sum or Average	5446.04					2315.38
Minimum of Months	383.79	2382.76		26.60	18.92	177.10	951.32		22.30	17.00
Maximum of Months	505.07	2662.94		31.70	23.28	204.88	951.37		26.00	21.61

Table of Contents
Report: ZONE HEATING SUMMARY
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE HEATING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]
January	74.53	1655.66	16-JAN-08:04	20.15
February	63.11	1637.79	15-FEB-08:05	19.75
March	54.25	1507.63	05-MAR-08:11	20.65
April	54.38	1386.12	02-APR-08:04	21.55
May	62.51	1416.81	10-MAY-08:15	20.45
June	63.40	1578.03	04-JUN-08:15	19.17
July	75.72	1666.92	16-JUL-08:08	18.08
August	78.93	1642.49	05-AUG-08:15	17.85
September	76.07	1736.95	12-SEP-08:04	17.90
October	85.05	1728.24	02-OCT-08:08	17.82
November	79.42	1820.11	04-NOV-08:08	19.10
December	76.14	1523.41	11-DEC-08:04	20.58

Annual Sum or Average	843.51
Minimum of Months	54.25	1386.12		17.82
Maximum of Months	85.05	1820.11		21.55

Table of Contents
Report: ZONE HEATING SUMMARY
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE HEATING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]
January	40.45	5636.01	16-JAN-06:02	17.85
February	36.04	5630.96	15-FEB-06:02	17.83
March	33.34	5377.21	05-MAR-06:03	18.63
April	33.62	5123.12	02-APR-06:03	19.05
May	32.99	5119.55	10-MAY-06:03	17.88
June	35.65	5175.88	17-JUN-06:03	16.95
July	38.49	5194.44	16-JUL-06:03	15.93
August	37.94	5125.66	08-AUG-06:03	15.85
September	36.43	5170.83	12-SEP-06:03	15.00
October	38.92	5612.21	04-OCT-06:02	15.98
November	37.73	5647.30	04-NOV-06:02	16.05
December	38.52	5617.26	13-DEC-06:02	17.55

Annual Sum or Average	440.12
Minimum of Months	32.99	5119.55		15.00
Maximum of Months	40.45	5647.30		19.05

Table of Contents
Report: ZONE HEATING SUMMARY
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE HEATING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]
January	14.09	2845.10	16-JAN-06:02	17.85
February	12.61	2842.70	15-FEB-06:02	17.83
March	11.78	2682.05	05-MAR-06:03	18.63
April	11.60	2451.54	02-APR-06:03	19.05
May	12.25	2451.61	10-MAY-06:03	17.88
June	11.87	2482.23	17-JUN-06:03	16.95
July	12.65	2497.21	16-JUL-06:03	15.93
August	12.92	2454.82	08-AUG-06:03	15.85
September	11.72	2492.71	12-SEP-06:03	15.00
October	8.57	2804.06	03-OCT-06:02	15.87
November	8.26	2753.98	13-NOV-06:03	18.07
December	12.62	2828.50	13-DEC-06:02	17.55

Annual Sum or Average	140.93
Minimum of Months	8.26	2451.54		15.00
Maximum of Months	14.09	2845.10		19.05

Table of Contents
Report: ZONE HEATING SUMMARY
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE HEATING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]
January	35.23	4866.48	16-JAN-06:02	17.85
February	30.49	4861.43	15-FEB-06:02	17.83
March	26.48	4627.29	05-MAR-06:03	18.63
April	24.59	4296.11	02-APR-06:03	19.05
May	25.55	4289.91	10-MAY-06:03	17.88
June	24.15	4340.66	17-JUN-06:03	16.95
July	25.83	4363.05	16-JUL-06:03	15.93
August	27.56	4296.96	08-AUG-06:03	15.85
September	26.38	4339.63	12-SEP-06:03	15.00
October	23.40	4823.46	03-OCT-06:02	15.87
November	26.97	4848.67	15-NOV-06:02	15.38
December	33.76	4847.72	13-DEC-06:02	17.55

Annual Sum or Average	330.39
Minimum of Months	23.40	4289.91		15.00
Maximum of Months	35.23	4866.48		19.05

Table of Contents
Report: ZONE HEATING SUMMARY
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE HEATING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]
January	17.76	2199.69	16-JAN-06:02	17.85
February	15.76	2198.20	15-FEB-06:02	17.83
March	14.44	2060.58	05-MAR-06:03	18.63
April	14.19	1779.96	02-APR-06:03	19.05
May	13.98	1780.16	10-MAY-06:03	17.88
June	14.99	1804.67	17-JUN-06:03	16.95
July	16.17	1820.56	16-JUL-06:03	15.93
August	15.93	1781.90	08-AUG-06:03	15.85
September	15.30	1816.80	12-SEP-06:03	15.00
October	16.55	2178.65	03-OCT-06:02	15.87
November	16.36	2201.24	15-NOV-06:02	15.38
December	16.59	2182.93	13-DEC-06:02	17.55

Annual Sum or Average	188.03
Minimum of Months	13.98	1779.96		15.00
Maximum of Months	17.76	2201.24		19.05

Table of Contents
Report: ZONE HEATING SUMMARY
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE HEATING ENERGY [kWh]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE HEATING RATE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]
January	69.82	5540.57	16-JAN-06:02	17.85
February	61.36	5537.22	15-FEB-06:02	17.83
March	60.75	5267.63	05-MAR-06:03	18.63
April	58.56	4735.39	02-APR-06:03	19.05
May	57.43	4684.72	10-MAY-06:03	17.88
June	54.40	4741.29	13-JUN-06:03	20.38
July	57.40	4741.67	16-JUL-06:03	15.93
August	53.79	4680.29	02-AUG-06:03	18.00
September	52.16	4697.56	11-SEP-06:03	15.72
October	60.41	5439.79	03-OCT-06:02	15.87
November	60.42	5495.34	04-NOV-06:02	16.05
December	65.28	5484.31	13-DEC-06:02	17.55

Annual Sum or Average	711.79
Minimum of Months	52.16	4680.29		15.72
Maximum of Months	69.82	5540.57		20.38

Table of Contents
Report: ZONE ELECTRIC SUMMARY
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE LIGHTS ELECTRIC ENERGY [kWh]	ZONE LIGHTS ELECTRIC ENERGY {Maximum}[W]	ZONE LIGHTS ELECTRIC ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {TIMESTAMP}
January	417.78	1584.00	01-JAN-10:15	240.68	950.40	01-JAN-09:15
February	365.27	1584.00	01-FEB-10:15	214.58	950.40	01-FEB-09:15
March	386.58	1584.00	01-MAR-10:15	233.42	950.40	01-MAR-09:15
April	400.28	1584.00	01-APR-10:15	231.98	950.40	01-APR-09:15
May	417.78	1584.00	01-MAY-10:15	240.68	950.40	01-MAY-09:15
June	369.07	1584.00	03-JUN-10:15	224.72	950.40	03-JUN-09:15
July	417.78	1584.00	01-JUL-10:15	240.68	950.40	01-JUL-09:15
August	402.18	1584.00	01-AUG-10:15	237.05	950.40	01-AUG-09:15
September	384.67	1584.00	02-SEP-10:15	228.35	950.40	02-SEP-09:15
October	417.78	1584.00	01-OCT-10:15	240.68	950.40	01-OCT-09:15
November	384.67	1584.00	01-NOV-10:15	228.35	950.40	01-NOV-09:15
December	402.18	1584.00	02-DEC-10:15	237.05	950.40	02-DEC-09:15

Annual Sum or Average	4766.02			2798.23
Minimum of Months	365.27	1584.00		214.58	950.40
Maximum of Months	417.78	1584.00		240.68	950.40

Table of Contents
Report: ZONE ELECTRIC SUMMARY
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE LIGHTS ELECTRIC ENERGY [kWh]	ZONE LIGHTS ELECTRIC ENERGY {Maximum}[W]	ZONE LIGHTS ELECTRIC ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {TIMESTAMP}
January	180.41	684.00	01-JAN-10:15	103.93	410.40	01-JAN-09:15
February	157.73	684.00	01-FEB-10:15	92.66	410.40	01-FEB-09:15
March	166.93	684.00	01-MAR-10:15	100.79	410.40	01-MAR-09:15
April	172.85	684.00	01-APR-10:15	100.17	410.40	01-APR-09:15
May	180.41	684.00	01-MAY-10:15	103.93	410.40	01-MAY-09:15
June	159.37	684.00	03-JUN-10:15	97.04	410.40	03-JUN-09:15
July	180.41	684.00	01-JUL-10:15	103.93	410.40	01-JUL-09:15
August	173.67	684.00	01-AUG-10:15	102.36	410.40	01-AUG-09:15
September	166.11	684.00	02-SEP-10:15	98.61	410.40	02-SEP-09:15
October	180.41	684.00	01-OCT-10:15	103.93	410.40	01-OCT-09:15
November	166.11	684.00	01-NOV-10:15	98.61	410.40	01-NOV-09:15
December	173.67	684.00	02-DEC-10:15	102.36	410.40	02-DEC-09:15

Annual Sum or Average	2058.05			1208.33
Minimum of Months	157.73	684.00		92.66	410.40
Maximum of Months	180.41	684.00		103.93	410.40

Table of Contents
Report: ZONE ELECTRIC SUMMARY
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE LIGHTS ELECTRIC ENERGY [kWh]	ZONE LIGHTS ELECTRIC ENERGY {Maximum}[W]	ZONE LIGHTS ELECTRIC ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {TIMESTAMP}
January	417.78	1584.00	01-JAN-10:15	240.68	950.40	01-JAN-09:15
February	365.27	1584.00	01-FEB-10:15	214.58	950.40	01-FEB-09:15
March	386.58	1584.00	01-MAR-10:15	233.42	950.40	01-MAR-09:15
April	400.28	1584.00	01-APR-10:15	231.98	950.40	01-APR-09:15
May	417.78	1584.00	01-MAY-10:15	240.68	950.40	01-MAY-09:15
June	369.07	1584.00	03-JUN-10:15	224.72	950.40	03-JUN-09:15
July	417.78	1584.00	01-JUL-10:15	240.68	950.40	01-JUL-09:15
August	402.18	1584.00	01-AUG-10:15	237.05	950.40	01-AUG-09:15
September	384.67	1584.00	02-SEP-10:15	228.35	950.40	02-SEP-09:15
October	417.78	1584.00	01-OCT-10:15	240.68	950.40	01-OCT-09:15
November	384.67	1584.00	01-NOV-10:15	228.35	950.40	01-NOV-09:15
December	402.18	1584.00	02-DEC-10:15	237.05	950.40	02-DEC-09:15

Annual Sum or Average	4766.02			2798.23
Minimum of Months	365.27	1584.00		214.58	950.40
Maximum of Months	417.78	1584.00		240.68	950.40

Table of Contents
Report: ZONE ELECTRIC SUMMARY
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE LIGHTS ELECTRIC ENERGY [kWh]	ZONE LIGHTS ELECTRIC ENERGY {Maximum}[W]	ZONE LIGHTS ELECTRIC ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {TIMESTAMP}
January	180.41	684.00	01-JAN-10:15	103.93	410.40	01-JAN-09:15
February	157.73	684.00	01-FEB-10:15	92.66	410.40	01-FEB-09:15
March	166.93	684.00	01-MAR-10:15	100.79	410.40	01-MAR-09:15
April	172.85	684.00	01-APR-10:15	100.17	410.40	01-APR-09:15
May	180.41	684.00	01-MAY-10:15	103.93	410.40	01-MAY-09:15
June	159.37	684.00	03-JUN-10:15	97.04	410.40	03-JUN-09:15
July	180.41	684.00	01-JUL-10:15	103.93	410.40	01-JUL-09:15
August	173.67	684.00	01-AUG-10:15	102.36	410.40	01-AUG-09:15
September	166.11	684.00	02-SEP-10:15	98.61	410.40	02-SEP-09:15
October	180.41	684.00	01-OCT-10:15	103.93	410.40	01-OCT-09:15
November	166.11	684.00	01-NOV-10:15	98.61	410.40	01-NOV-09:15
December	173.67	684.00	02-DEC-10:15	102.36	410.40	02-DEC-09:15

Annual Sum or Average	2058.05			1208.33
Minimum of Months	157.73	684.00		92.66	410.40
Maximum of Months	180.41	684.00		103.93	410.40

Table of Contents
Report: ZONE ELECTRIC SUMMARY
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE LIGHTS ELECTRIC ENERGY [kWh]	ZONE LIGHTS ELECTRIC ENERGY {Maximum}[W]	ZONE LIGHTS ELECTRIC ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT ELECTRIC ENERGY {TIMESTAMP}
January	781.75	2964.00	01-JAN-10:15	450.37	1778.40	01-JAN-09:15
February	683.50	2964.00	01-FEB-10:15	401.52	1778.40	01-FEB-09:15
March	723.36	2964.00	01-MAR-10:15	436.78	1778.40	01-MAR-09:15
April	749.00	2964.00	01-APR-10:15	434.09	1778.40	01-APR-09:15
May	781.75	2964.00	01-MAY-10:15	450.37	1778.40	01-MAY-09:15
June	690.61	2964.00	03-JUN-10:15	420.49	1778.40	03-JUN-09:15
July	781.75	2964.00	01-JUL-10:15	450.37	1778.40	01-JUL-09:15
August	752.56	2964.00	01-AUG-10:15	443.57	1778.40	01-AUG-09:15
September	719.81	2964.00	02-SEP-10:15	427.29	1778.40	02-SEP-09:15
October	781.75	2964.00	01-OCT-10:15	450.37	1778.40	01-OCT-09:15
November	719.81	2964.00	01-NOV-10:15	427.29	1778.40	01-NOV-09:15
December	752.56	2964.00	02-DEC-10:15	443.57	1778.40	02-DEC-09:15

Annual Sum or Average	8918.23			5236.08
Minimum of Months	683.50	2964.00		401.52	1778.40
Maximum of Months	781.75	2964.00		450.37	1778.40

Table of Contents
Report: SPACE GAINS
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY [kWh]	ZONE LIGHTS TOTAL HEATING ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY [kWh]
January	281.79	417.78	240.68	3.55	0.27
February	245.03	365.27	214.58	2.04	0.13
March	257.28	386.58	233.42	2.43	0.07
April	269.53	400.28	231.98	0.00	0.00
May	281.79	417.78	240.68	0.00	0.00
June	245.03	369.07	224.72	0.00	0.00
July	281.79	417.78	240.68	0.00	0.00
August	269.53	402.18	237.05	0.00	0.00
September	257.28	384.67	228.35	0.00	0.00
October	281.79	417.78	240.68	0.00	0.00
November	257.28	384.67	228.35	2.66	2.41
December	269.53	402.18	237.05	4.13	1.03

Annual Sum or Average	3197.66	4766.02	2798.23	14.81	3.91
Minimum of Months	245.03	365.27	214.58	0.00	0.00
Maximum of Months	281.79	417.78	240.68	4.13	2.41

Table of Contents
Report: SPACE GAINS
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY [kWh]	ZONE LIGHTS TOTAL HEATING ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY [kWh]
January	128.08	180.41	103.93	1.49	0.21
February	111.38	157.73	92.66	0.85	0.10
March	116.95	166.93	100.79	0.91	0.07
April	122.52	172.85	100.17	0.00	0.00
May	128.08	180.41	103.93	0.00	0.00
June	111.38	159.37	97.04	0.00	0.00
July	128.08	180.41	103.93	0.00	0.00
August	122.52	173.67	102.36	0.00	0.00
September	116.95	166.11	98.61	0.00	0.00
October	128.08	180.41	103.93	0.00	0.00
November	116.95	166.11	98.61	1.09	1.50
December	122.52	173.67	102.36	1.55	0.70

Annual Sum or Average	1453.48	2058.05	1208.33	5.90	2.59
Minimum of Months	111.38	157.73	92.66	0.00	0.00
Maximum of Months	128.08	180.41	103.93	1.55	1.50

Table of Contents
Report: SPACE GAINS
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY [kWh]	ZONE LIGHTS TOTAL HEATING ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY [kWh]
January	281.79	417.78	240.68	4.13	0.24
February	245.03	365.27	214.58	2.16	0.12
March	257.28	386.58	233.42	2.29	0.08
April	269.53	400.28	231.98	0.00	0.00
May	281.79	417.78	240.68	0.00	0.00
June	245.03	369.07	224.72	0.00	0.00
July	281.79	417.78	240.68	0.00	0.00
August	269.53	402.18	237.05	0.00	0.00
September	257.28	384.67	228.35	0.00	0.00
October	281.79	417.78	240.68	0.00	0.00
November	257.28	384.67	228.35	2.95	2.33
December	269.53	402.18	237.05	4.55	0.88

Annual Sum or Average	3197.66	4766.02	2798.23	16.08	3.65
Minimum of Months	245.03	365.27	214.58	0.00	0.00
Maximum of Months	281.79	417.78	240.68	4.55	2.33

Table of Contents
Report: SPACE GAINS
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY [kWh]	ZONE LIGHTS TOTAL HEATING ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY [kWh]
January	128.08	180.41	103.93	1.72	0.11
February	111.38	157.73	92.66	0.91	0.06
March	116.95	166.93	100.79	0.90	0.10
April	122.52	172.85	100.17	0.00	0.00
May	128.08	180.41	103.93	0.00	0.00
June	111.38	159.37	97.04	0.00	0.00
July	128.08	180.41	103.93	0.00	0.00
August	122.52	173.67	102.36	0.00	0.00
September	116.95	166.11	98.61	0.00	0.00
October	128.08	180.41	103.93	0.00	0.00
November	116.95	166.11	98.61	1.40	1.04
December	122.52	173.67	102.36	2.04	0.40

Annual Sum or Average	1453.48	2058.05	1208.33	6.96	1.71
Minimum of Months	111.38	157.73	92.66	0.00	0.00
Maximum of Months	128.08	180.41	103.93	2.04	1.04

Table of Contents
Report: SPACE GAINS
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY [kWh]	ZONE LIGHTS TOTAL HEATING ENERGY [kWh]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY [kWh]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY [kWh]
January	512.34	781.75	450.37	8.71	0.55
February	445.51	683.50	401.52	4.72	0.26
March	467.79	723.36	436.78	6.14	0.13
April	490.06	749.00	434.09	0.00	0.00
May	512.34	781.75	450.37	0.00	0.00
June	445.51	690.61	420.49	0.00	0.00
July	512.34	781.75	450.37	0.00	0.00
August	490.06	752.56	443.57	0.00	0.00
September	467.79	719.81	427.29	0.00	0.00
October	512.34	781.75	450.37	0.00	0.00
November	467.79	719.81	427.29	6.23	4.80
December	490.06	752.56	443.57	9.97	2.07

Annual Sum or Average	5813.93	8918.23	5236.08	35.78	7.82
Minimum of Months	445.51	683.50	401.52	0.00	0.00
Maximum of Months	512.34	781.75	450.37	9.97	4.80

Table of Contents
Report: PEAK SPACE GAINS
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY {Maximum}[W]	ZONE PEOPLE TOTAL HEATING ENERGY {TIMESTAMP}	ZONE LIGHTS TOTAL HEATING ENERGY {Maximum}[W]	ZONE LIGHTS TOTAL HEATING ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {TIMESTAMP}	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {TIMESTAMP}	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {TIMESTAMP}
January	1289.64	01-JAN-08:15	1584.00	01-JAN-10:15	950.40	01-JAN-09:15	0.00	0.00	0.00	0.00	72.93	21-JAN-13:00	12.54	15-JAN-06:10
February	1289.64	01-FEB-08:15	1584.00	01-FEB-10:15	950.40	01-FEB-09:15	0.00	0.00	0.00	0.00	32.65	15-FEB-16:00	8.65	16-FEB-04:00
March	1289.64	01-MAR-08:15	1584.00	01-MAR-10:15	950.40	01-MAR-09:15	0.00	0.00	0.00	0.00	41.56	31-MAR-13:53	4.30	09-MAR-03:00
April	1289.64	01-APR-08:15	1584.00	01-APR-10:15	950.40	01-APR-09:15	0.00	0.00	0.00	0.00	0.00	01-APR-00:15	0.00	01-APR-00:15
May	1289.64	01-MAY-08:15	1584.00	01-MAY-10:15	950.40	01-MAY-09:15	0.00	0.00	0.00	0.00	0.00	01-MAY-00:15	0.00	01-MAY-00:15
June	1289.64	03-JUN-08:15	1584.00	03-JUN-10:15	950.40	03-JUN-09:15	0.00	0.00	0.00	0.00	0.00	01-JUN-00:15	0.00	01-JUN-00:15
July	1289.64	01-JUL-08:15	1584.00	01-JUL-10:15	950.40	01-JUL-09:15	0.00	0.00	0.00	0.00	0.00	01-JUL-00:15	0.00	01-JUL-00:15
August	1289.64	01-AUG-08:15	1584.00	01-AUG-10:15	950.40	01-AUG-09:15	0.00	0.00	0.00	0.00	0.00	01-AUG-00:15	0.00	01-AUG-00:15
September	1289.64	02-SEP-08:15	1584.00	02-SEP-10:15	950.40	02-SEP-09:15	0.00	0.00	0.00	0.00	0.00	01-SEP-00:15	0.00	01-SEP-00:15
October	1289.64	01-OCT-08:15	1584.00	01-OCT-10:15	950.40	01-OCT-09:15	0.00	0.00	0.00	0.00	0.00	01-OCT-00:15	0.00	01-OCT-00:15
November	1289.64	01-NOV-08:15	1584.00	01-NOV-10:15	950.40	01-NOV-09:15	0.00	0.00	0.00	0.00	114.63	11-NOV-14:00	53.10	04-NOV-06:53
December	1289.64	02-DEC-08:15	1584.00	02-DEC-10:15	950.40	02-DEC-09:15	0.00	0.00	0.00	0.00	91.48	12-DEC-15:00	40.18	13-DEC-04:00

Annual Sum or Average
Minimum of Months	1289.64		1584.00		950.40		0.00	0.00	0.00	0.00	0.00		0.00
Maximum of Months	1289.64		1584.00		950.40		0.00	0.00	0.00	0.00	114.63		53.10

Table of Contents
Report: PEAK SPACE GAINS
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY {Maximum}[W]	ZONE PEOPLE TOTAL HEATING ENERGY {TIMESTAMP}	ZONE LIGHTS TOTAL HEATING ENERGY {Maximum}[W]	ZONE LIGHTS TOTAL HEATING ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {TIMESTAMP}	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {TIMESTAMP}	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {TIMESTAMP}
January	586.20	01-JAN-08:15	684.00	01-JAN-10:15	410.40	01-JAN-09:15	0.00	0.00	0.00	0.00	31.90	21-JAN-13:00	8.77	19-JAN-10:00
February	586.20	01-FEB-08:15	684.00	01-FEB-10:15	410.40	01-FEB-09:15	0.00	0.00	0.00	0.00	14.29	15-FEB-16:00	7.13	16-FEB-10:15
March	586.20	01-MAR-08:15	684.00	01-MAR-10:15	410.40	01-MAR-09:15	0.00	0.00	0.00	0.00	16.64	31-MAR-17:00	3.72	09-MAR-11:23
April	586.20	01-APR-08:15	684.00	01-APR-10:15	410.40	01-APR-09:15	0.00	0.00	0.00	0.00	0.00	01-APR-00:15	0.00	01-APR-00:15
May	586.20	01-MAY-08:15	684.00	01-MAY-10:15	410.40	01-MAY-09:15	0.00	0.00	0.00	0.00	0.00	01-MAY-00:15	0.00	01-MAY-00:15
June	586.20	03-JUN-08:15	684.00	03-JUN-10:15	410.40	03-JUN-09:15	0.00	0.00	0.00	0.00	0.00	01-JUN-00:15	0.00	01-JUN-00:15
July	586.20	01-JUL-08:15	684.00	01-JUL-10:15	410.40	01-JUL-09:15	0.00	0.00	0.00	0.00	0.00	01-JUL-00:15	0.00	01-JUL-00:15
August	586.20	01-AUG-08:15	684.00	01-AUG-10:15	410.40	01-AUG-09:15	0.00	0.00	0.00	0.00	0.00	01-AUG-00:15	0.00	01-AUG-00:15
September	586.20	02-SEP-08:15	684.00	02-SEP-10:15	410.40	02-SEP-09:15	0.00	0.00	0.00	0.00	0.00	01-SEP-00:15	0.00	01-SEP-00:15
October	586.20	01-OCT-08:15	684.00	01-OCT-10:15	410.40	01-OCT-09:15	0.00	0.00	0.00	0.00	0.00	01-OCT-00:15	0.00	01-OCT-00:15
November	586.20	01-NOV-08:15	684.00	01-NOV-10:15	410.40	01-NOV-09:15	0.00	0.00	0.00	0.00	50.15	11-NOV-14:00	36.42	02-NOV-09:00
December	586.20	02-DEC-08:15	684.00	02-DEC-10:15	410.40	02-DEC-09:15	0.00	0.00	0.00	0.00	41.31	12-DEC-15:45	20.90	07-DEC-09:45

Annual Sum or Average
Minimum of Months	586.20		684.00		410.40		0.00	0.00	0.00	0.00	0.00		0.00
Maximum of Months	586.20		684.00		410.40		0.00	0.00	0.00	0.00	50.15		36.42

Table of Contents
Report: PEAK SPACE GAINS
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY {Maximum}[W]	ZONE PEOPLE TOTAL HEATING ENERGY {TIMESTAMP}	ZONE LIGHTS TOTAL HEATING ENERGY {Maximum}[W]	ZONE LIGHTS TOTAL HEATING ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {TIMESTAMP}	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {TIMESTAMP}	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {TIMESTAMP}
January	1289.64	01-JAN-08:15	1584.00	01-JAN-10:15	950.40	01-JAN-09:15	0.00	0.00	0.00	0.00	74.14	21-JAN-13:00	12.54	15-JAN-06:10
February	1289.64	01-FEB-08:15	1584.00	01-FEB-10:15	950.40	01-FEB-09:15	0.00	0.00	0.00	0.00	32.65	15-FEB-16:00	8.60	16-FEB-04:00
March	1289.64	01-MAR-08:15	1584.00	01-MAR-10:15	950.40	01-MAR-09:15	0.00	0.00	0.00	0.00	38.00	31-MAR-16:00	4.29	09-MAR-03:00
April	1289.64	01-APR-08:15	1584.00	01-APR-10:15	950.40	01-APR-09:15	0.00	0.00	0.00	0.00	0.00	01-APR-00:15	0.00	01-APR-00:15
May	1289.64	01-MAY-08:15	1584.00	01-MAY-10:15	950.40	01-MAY-09:15	0.00	0.00	0.00	0.00	0.00	01-MAY-00:15	0.00	01-MAY-00:15
June	1289.64	03-JUN-08:15	1584.00	03-JUN-10:15	950.40	03-JUN-09:15	0.00	0.00	0.00	0.00	0.00	01-JUN-00:15	0.00	01-JUN-00:15
July	1289.64	01-JUL-08:15	1584.00	01-JUL-10:15	950.40	01-JUL-09:15	0.00	0.00	0.00	0.00	0.00	01-JUL-00:15	0.00	01-JUL-00:15
August	1289.64	01-AUG-08:15	1584.00	01-AUG-10:15	950.40	01-AUG-09:15	0.00	0.00	0.00	0.00	0.00	01-AUG-00:15	0.00	01-AUG-00:15
September	1289.64	02-SEP-08:15	1584.00	02-SEP-10:15	950.40	02-SEP-09:15	0.00	0.00	0.00	0.00	0.00	01-SEP-00:15	0.00	01-SEP-00:15
October	1289.64	01-OCT-08:15	1584.00	01-OCT-10:15	950.40	01-OCT-09:15	0.00	0.00	0.00	0.00	0.00	01-OCT-00:15	0.00	01-OCT-00:15
November	1289.64	01-NOV-08:15	1584.00	01-NOV-10:15	950.40	01-NOV-09:15	0.00	0.00	0.00	0.00	114.63	11-NOV-14:00	56.33	02-NOV-07:00
December	1289.64	02-DEC-08:15	1584.00	02-DEC-10:15	950.40	02-DEC-09:15	0.00	0.00	0.00	0.00	94.43	12-DEC-15:45	39.64	13-DEC-04:00

Annual Sum or Average
Minimum of Months	1289.64		1584.00		950.40		0.00	0.00	0.00	0.00	0.00		0.00
Maximum of Months	1289.64		1584.00		950.40		0.00	0.00	0.00	0.00	114.63		56.33

Table of Contents
Report: PEAK SPACE GAINS
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY {Maximum}[W]	ZONE PEOPLE TOTAL HEATING ENERGY {TIMESTAMP}	ZONE LIGHTS TOTAL HEATING ENERGY {Maximum}[W]	ZONE LIGHTS TOTAL HEATING ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {TIMESTAMP}	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {TIMESTAMP}	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {TIMESTAMP}
January	586.20	01-JAN-08:15	684.00	01-JAN-10:15	410.40	01-JAN-09:15	0.00	0.00	0.00	0.00	37.96	21-JAN-13:00	5.49	15-JAN-06:13
February	586.20	01-FEB-08:15	684.00	01-FEB-10:15	410.40	01-FEB-09:15	0.00	0.00	0.00	0.00	14.28	15-FEB-16:00	3.93	16-FEB-17:53
March	586.20	01-MAR-08:15	684.00	01-MAR-10:15	410.40	01-MAR-09:15	0.00	0.00	0.00	0.00	11.57	31-MAR-13:38	9.77	09-MAR-17:53
April	586.20	01-APR-08:15	684.00	01-APR-10:15	410.40	01-APR-09:15	0.00	0.00	0.00	0.00	0.00	01-APR-00:15	0.00	01-APR-00:15
May	586.20	01-MAY-08:15	684.00	01-MAY-10:15	410.40	01-MAY-09:15	0.00	0.00	0.00	0.00	0.00	01-MAY-00:15	0.00	01-MAY-00:15
June	586.20	03-JUN-08:15	684.00	03-JUN-10:15	410.40	03-JUN-09:15	0.00	0.00	0.00	0.00	0.00	01-JUN-00:15	0.00	01-JUN-00:15
July	586.20	01-JUL-08:15	684.00	01-JUL-10:15	410.40	01-JUL-09:15	0.00	0.00	0.00	0.00	0.00	01-JUL-00:15	0.00	01-JUL-00:15
August	586.20	01-AUG-08:15	684.00	01-AUG-10:15	410.40	01-AUG-09:15	0.00	0.00	0.00	0.00	0.00	01-AUG-00:15	0.00	01-AUG-00:15
September	586.20	02-SEP-08:15	684.00	02-SEP-10:15	410.40	02-SEP-09:15	0.00	0.00	0.00	0.00	0.00	01-SEP-00:15	0.00	01-SEP-00:15
October	586.20	01-OCT-08:15	684.00	01-OCT-10:15	410.40	01-OCT-09:15	0.00	0.00	0.00	0.00	0.00	01-OCT-00:15	0.00	01-OCT-00:15
November	586.20	01-NOV-08:15	684.00	01-NOV-10:15	410.40	01-NOV-09:15	0.00	0.00	0.00	0.00	50.17	11-NOV-14:00	23.23	02-NOV-07:00
December	586.20	02-DEC-08:15	684.00	02-DEC-10:15	410.40	02-DEC-09:15	0.00	0.00	0.00	0.00	41.32	12-DEC-15:45	17.98	13-DEC-04:00

Annual Sum or Average
Minimum of Months	586.20		684.00		410.40		0.00	0.00	0.00	0.00	0.00		0.00
Maximum of Months	586.20		684.00		410.40		0.00	0.00	0.00	0.00	50.17		23.23

Table of Contents
Report: PEAK SPACE GAINS
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE PEOPLE TOTAL HEATING ENERGY {Maximum}[W]	ZONE PEOPLE TOTAL HEATING ENERGY {TIMESTAMP}	ZONE LIGHTS TOTAL HEATING ENERGY {Maximum}[W]	ZONE LIGHTS TOTAL HEATING ENERGY {TIMESTAMP}	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {Maximum}[W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {TIMESTAMP}	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {TIMESTAMP}	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {Maximum}[W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {TIMESTAMP}
January	2344.80	01-JAN-08:15	2964.00	01-JAN-10:15	1778.40	01-JAN-09:15	0.00	0.00	0.00	0.00	141.30	21-JAN-13:00	24.91	15-JAN-06:08
February	2344.80	01-FEB-08:15	2964.00	01-FEB-10:15	1778.40	01-FEB-09:15	0.00	0.00	0.00	0.00	80.18	16-FEB-13:53	18.83	16-FEB-04:00
March	2344.80	01-MAR-08:15	2964.00	01-MAR-10:15	1778.40	01-MAR-09:15	0.00	0.00	0.00	0.00	117.65	31-MAR-13:53	9.34	09-MAR-03:00
April	2344.80	01-APR-08:15	2964.00	01-APR-10:15	1778.40	01-APR-09:15	0.00	0.00	0.00	0.00	0.00	01-APR-00:15	0.00	01-APR-00:15
May	2344.80	01-MAY-08:15	2964.00	01-MAY-10:15	1778.40	01-MAY-09:15	0.00	0.00	0.00	0.00	0.00	01-MAY-00:15	0.00	01-MAY-00:15
June	2344.80	03-JUN-08:15	2964.00	03-JUN-10:15	1778.40	03-JUN-09:15	0.00	0.00	0.00	0.00	0.00	01-JUN-00:15	0.00	01-JUN-00:15
July	2344.80	01-JUL-08:15	2964.00	01-JUL-10:15	1778.40	01-JUL-09:15	0.00	0.00	0.00	0.00	0.00	01-JUL-00:15	0.00	01-JUL-00:15
August	2344.80	01-AUG-08:15	2964.00	01-AUG-10:15	1778.40	01-AUG-09:15	0.00	0.00	0.00	0.00	0.00	01-AUG-00:15	0.00	01-AUG-00:15
September	2344.80	02-SEP-08:15	2964.00	02-SEP-10:15	1778.40	02-SEP-09:15	0.00	0.00	0.00	0.00	0.00	01-SEP-00:15	0.00	01-SEP-00:15
October	2344.80	01-OCT-08:15	2964.00	01-OCT-10:15	1778.40	01-OCT-09:15	0.00	0.00	0.00	0.00	0.00	01-OCT-00:15	0.00	01-OCT-00:15
November	2344.80	01-NOV-08:15	2964.00	01-NOV-10:15	1778.40	01-NOV-09:15	0.00	0.00	0.00	0.00	222.10	11-NOV-14:00	108.18	02-NOV-06:53
December	2344.80	02-DEC-08:15	2964.00	02-DEC-10:15	1778.40	02-DEC-09:15	0.00	0.00	0.00	0.00	273.92	14-DEC-12:00	85.53	13-DEC-04:00

Annual Sum or Average
Minimum of Months	2344.80		2964.00		1778.40		0.00	0.00	0.00	0.00	0.00		0.00
Maximum of Months	2344.80		2964.00		1778.40		0.00	0.00	0.00	0.00	273.92		108.18

Table of Contents
Report: SPACE GAIN COMPONENTS AT COOLING PEAK
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	ZONE PEOPLE TOTAL HEATING ENERGY []	ZONE LIGHTS TOTAL HEATING ENERGY []	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY []	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY []	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY []
January	3648.48	04-JAN-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	3300.76	08-FEB-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	3516.08	05-MAR-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	3047.85	08-APR-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	3242.25	20-MAY-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	2840.03	25-JUN-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	2392.95	17-JUL-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	3154.90	30-AUG-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	2974.70	03-SEP-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	3324.24	18-OCT-16:00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	3723.81	07-NOV-15:45	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	3273.56	20-DEC-15:45	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average
Minimum of Months	2392.95		0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	3723.81		0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: SPACE GAIN COMPONENTS AT COOLING PEAK
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	ZONE PEOPLE TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE LIGHTS TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {AT MAX/MIN} [W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {AT MAX/MIN} [W]
January	2917.33	04-JAN-17:30	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	9.33	0.00
February	2578.71	08-FEB-17:15	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	3.13	0.00
March	2434.18	05-MAR-17:30	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	6.41	0.00
April	2455.18	10-APR-15:00	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	0.00	0.00
May	2418.36	02-MAY-14:45	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	0.00	0.00
June	2243.38	25-JUN-15:00	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	0.00	0.00
July	2292.55	29-JUL-14:30	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	0.00	0.00
August	2434.15	19-AUG-14:45	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	0.00	0.00
September	2525.29	19-SEP-17:30	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	0.00	0.00
October	2542.73	30-OCT-16:45	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	0.00	0.00
November	2664.85	15-NOV-16:45	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	15.48	0.00
December	2883.33	20-DEC-17:30	1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	4.65	0.00

Annual Sum or Average
Minimum of Months	2243.38		1289.64	1584.00	528.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	2917.33		1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	15.48	0.00

Table of Contents
Report: SPACE GAIN COMPONENTS AT COOLING PEAK
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	ZONE PEOPLE TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE LIGHTS TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {AT MAX/MIN} [W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {AT MAX/MIN} [W]
January	1883.41	23-JAN-10:30	1172.40	1368.00	820.80	0.00	0.00	0.00	0.00	0.95	0.00
February	1754.49	22-FEB-10:30	586.20	684.00	410.40	0.00	0.00	0.00	0.00	2.65	0.00
March	1747.51	18-MAR-10:15	586.20	684.00	410.40	0.00	0.00	0.00	0.00	1.12	0.00
April	1939.82	02-APR-10:15	1172.40	1368.00	820.80	0.00	0.00	0.00	0.00	0.00	0.00
May	1500.02	20-MAY-09:45	586.20	649.80	410.40	0.00	0.00	0.00	0.00	0.00	0.00
June	1316.99	12-JUN-10:15	586.20	684.00	410.40	0.00	0.00	0.00	0.00	0.00	0.00
July	1473.00	12-JUL-10:30	586.20	684.00	410.40	0.00	0.00	0.00	0.00	0.00	0.00
August	1774.01	30-AUG-09:45	1172.40	1299.60	820.80	0.00	0.00	0.00	0.00	0.00	0.00
September	1935.05	30-SEP-09:45	1172.40	1299.60	820.80	0.00	0.00	0.00	0.00	0.00	0.00
October	1726.78	11-OCT-09:45	1172.40	1299.60	820.80	0.00	0.00	0.00	0.00	0.00	0.00
November	1760.64	07-NOV-09:53	1172.40	1299.60	820.80	0.00	0.00	0.00	0.00	0.00	1.04
December	1847.53	10-DEC-10:15	1172.40	1368.00	820.80	0.00	0.00	0.00	0.00	1.86	0.00

Annual Sum or Average
Minimum of Months	1316.99		586.20	649.80	410.40	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	1939.82		1172.40	1368.00	820.80	0.00	0.00	0.00	0.00	2.65	1.04

Table of Contents
Report: SPACE GAIN COMPONENTS AT COOLING PEAK
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	ZONE PEOPLE TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE LIGHTS TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {AT MAX/MIN} [W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {AT MAX/MIN} [W]
January	2613.97	23-JAN-14:30	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	12.96	0.00
February	2674.54	22-FEB-14:15	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	19.30	0.00
March	3612.58	27-MAR-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	6.56	0.00
April	4294.09	22-APR-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
May	4778.51	21-MAY-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
June	5213.34	12-JUN-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
July	5496.50	12-JUL-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
August	5267.66	01-AUG-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
September	3790.89	09-SEP-10:30	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
October	2551.38	03-OCT-10:45	1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	0.00	0.00
November	2494.27	11-NOV-14:15	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	108.85	0.00
December	2453.15	10-DEC-14:15	1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	10.09	0.00

Annual Sum or Average
Minimum of Months	2453.15		1289.64	1584.00	844.80	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	5496.50		1289.64	1584.00	950.40	0.00	0.00	0.00	0.00	108.85	0.00

Table of Contents
Report: SPACE GAIN COMPONENTS AT COOLING PEAK
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	ZONE PEOPLE TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE LIGHTS TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {AT MAX/MIN} [W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {AT MAX/MIN} [W]
January	1878.98	25-JAN-17:00	586.20	684.00	228.00	0.00	0.00	0.00	0.00	2.33	0.00
February	1743.88	08-FEB-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	1.81	0.00
March	2299.66	05-MAR-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	4.13	0.00
April	2664.64	15-APR-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
May	2917.93	20-MAY-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
June	2808.97	25-JUN-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
July	2691.20	22-JUL-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
August	2800.06	20-AUG-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
September	2669.98	05-SEP-16:30	586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
October	2445.14	07-OCT-16:00	586.20	684.00	319.20	0.00	0.00	0.00	0.00	0.00	0.00
November	2086.90	13-NOV-16:00	586.20	684.00	319.20	0.00	0.00	0.00	0.00	29.54	0.00
December	1741.88	17-DEC-16:45	586.20	684.00	228.00	0.00	0.00	0.00	0.00	31.88	0.00

Annual Sum or Average
Minimum of Months	1741.88		586.20	684.00	228.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	2917.93		586.20	684.00	319.20	0.00	0.00	0.00	0.00	31.88	0.00

Table of Contents
Report: SPACE GAIN COMPONENTS AT COOLING PEAK
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE AIR SYSTEM SENSIBLE COOLING RATE {Maximum}[W]	ZONE AIR SYSTEM SENSIBLE COOLING RATE {TIMESTAMP}	ZONE PEOPLE TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE LIGHTS TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE ELECTRIC EQUIPMENT TOTAL HEATING ENERGY {AT MAX/MIN} [W]	ZONE GAS EQUIPMENT TOTAL HEATING ENERGY []	ZONE HOT WATER EQUIPMENT TOTAL HEATING ENERGY []	ZONE STEAM EQUIPMENT TOTAL HEATING ENERGY []	ZONE OTHER EQUIPMENT TOTAL HEATING ENERGY []	ZONE INFILTRATION SENSIBLE HEAT GAIN ENERGY {AT MAX/MIN} [W]	ZONE INFILTRATION SENSIBLE HEAT LOSS ENERGY {AT MAX/MIN} [W]
January	2382.76	10-JAN-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	125.22	0.00
February	2409.97	27-FEB-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	29.29	0.00
March	2432.63	21-MAR-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	25.16	0.00
April	2497.49	08-APR-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
May	2573.70	20-MAY-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
June	2567.76	25-JUN-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
July	2561.16	17-JUL-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
August	2647.10	19-AUG-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
September	2662.94	03-SEP-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
October	2527.89	11-OCT-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
November	2549.62	11-NOV-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	175.90	0.00
December	2543.78	12-DEC-15:00	2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	182.46	0.00

Annual Sum or Average
Minimum of Months	2382.76		2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	2662.94		2344.80	2964.00	1580.80	0.00	0.00	0.00	0.00	182.46	0.00

Table of Contents
Report: ENERGY CONSUMPTION - ELECTRICITY & NATURAL GAS
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ELECTRICITY:FACILITY [kWh]	ELECTRICITY:FACILITY {Maximum}[W]	ELECTRICITY:FACILITY {TIMESTAMP}	GAS:FACILITY [kWh]	GAS:FACILITY {Maximum}[W]	GAS:FACILITY {TIMESTAMP}
January	4417.78	18092.27	21-JAN-10:00	4356.21	30118.07	16-JAN-06:15
February	3929.80	19431.05	22-FEB-15:00	3912.35	30247.22	15-FEB-06:15
March	4294.77	20112.67	22-MAR-10:00	4270.06	24570.21	05-MAR-06:15
April	4562.30	19772.28	11-APR-14:00	4398.69	26871.52	30-APR-06:15
May	4706.66	19267.76	06-MAY-10:00	4591.24	30234.22	10-MAY-06:15
June	4057.75	18884.57	19-JUN-14:00	4375.50	30668.56	04-JUN-06:15
July	4534.89	18428.18	29-JUL-14:00	4611.68	30995.82	16-JUL-06:15
August	4324.56	18435.29	01-AUG-10:00	4569.54	30051.10	05-AUG-06:15
September	4133.78	18469.92	04-SEP-10:00	4430.32	31443.99	12-SEP-06:15
October	4216.32	17526.28	11-OCT-14:00	4340.85	27572.96	02-OCT-06:15
November	3924.79	17577.38	11-NOV-14:00	4203.10	27820.70	15-NOV-06:15
December	4141.10	17753.05	19-DEC-14:00	4338.40	27110.21	13-DEC-06:15

Annual Sum or Average	51244.50			52397.95
Minimum of Months	3924.79	17526.28		3912.35	24570.21
Maximum of Months	4706.66	20112.67		4611.68	31443.99

Table of Contents
Report: ENERGY CONSUMPTION - ELECTRICITY GENERATED & PROPANE
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ELECTRICITYPRODUCED:FACILITY [kWh]	ELECTRICITYPRODUCED:FACILITY {Maximum}[W]	ELECTRICITYPRODUCED:FACILITY {TIMESTAMP}	PROPANE:FACILITY []	PROPANE:FACILITY []
January	1006.55	1446.12	24-JAN-05:00	0.00	0.00
February	908.75	1444.71	09-FEB-05:00	0.00	0.00
March	1003.67	1436.24	09-MAR-05:00	0.00	0.00
April	974.46	1437.65	30-APR-05:00	0.00	0.00
May	1008.93	1443.30	10-MAY-05:00	0.00	0.00
June	991.56	1465.85	09-JUN-05:00	0.00	0.00
July	1026.85	1470.08	16-JUL-05:00	0.00	0.00
August	1028.59	1481.34	05-AUG-05:00	0.00	0.00
September	1000.58	1484.15	12-SEP-05:00	0.00	0.00
October	1028.57	1478.52	02-OCT-05:00	0.00	0.00
November	993.72	1481.34	15-NOV-05:00	0.00	0.00
December	1012.72	1454.58	28-DEC-05:00	0.00	0.00

Annual Sum or Average	11984.96
Minimum of Months	908.75	1436.24		0.00	0.00
Maximum of Months	1028.59	1484.15		0.00	0.00

Table of Contents
Report: ENERGY CONSUMPTION - PURCHASED HEATING & COOLING
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	DISTRICTCOOLING:FACILITY []	DISTRICTCOOLING:FACILITY []	DISTRICTHEATING:FACILITY [kWh]	DISTRICTHEATING:FACILITY {Maximum}[W]	DISTRICTHEATING:FACILITY {TIMESTAMP}
January	0.00	0.00	804.57	4747.65	01-JAN-12:15
February	0.00	0.00	726.71	4747.65	01-FEB-12:15
March	0.00	0.00	804.57	4747.65	01-MAR-12:15
April	0.00	0.00	778.61	4747.65	01-APR-12:15
May	0.00	0.00	804.57	4747.65	01-MAY-12:15
June	0.00	0.00	778.61	4747.65	01-JUN-12:15
July	0.00	0.00	804.57	4747.65	01-JUL-12:15
August	0.00	0.00	804.57	4747.65	01-AUG-12:15
September	0.00	0.00	778.61	4747.65	01-SEP-12:15
October	0.00	0.00	804.57	4747.65	01-OCT-12:15
November	0.00	0.00	778.61	4747.65	01-NOV-12:15
December	0.00	0.00	804.57	4747.65	01-DEC-12:15

Annual Sum or Average			9473.13
Minimum of Months	0.00	0.00	726.71	4747.65
Maximum of Months	0.00	0.00	804.57	4747.65

Table of Contents
Report: END-USE ENERGY CONSUMPTION - ELECTRICITY
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	INTERIORLIGHTS:ELECTRICITY [kWh]	EXTERIORLIGHTS:ELECTRICITY []	INTERIOREQUIPMENT:ELECTRICITY [kWh]	EXTERIOREQUIPMENT:ELECTRICITY []	FANS:ELECTRICITY [kWh]	PUMPS:ELECTRICITY [kWh]	HEATING:ELECTRICITY [kWh]	COOLING:ELECTRICITY [kWh]	HEATREJECTION:ELECTRICITY []	HUMIDIFIER:ELECTRICITY []	HEATRECOVERY:ELECTRICITY []	WATERSYSTEMS:ELECTRICITY []	COGENERATION:ELECTRICITY []
January	1978.12	0.00	1139.60	0.00	205.50	42.45	0.00	1052.10	0.00	0.00	0.00	0.00	0.00
February	1729.50	0.00	1016.00	0.00	180.40	37.68	0.00	966.22	0.00	0.00	0.00	0.00	0.00
March	1830.37	0.00	1105.20	0.00	190.13	41.93	0.00	1127.13	0.00	0.00	0.00	0.00	0.00
April	1895.25	0.00	1098.40	0.00	187.86	74.08	0.00	1306.72	0.00	0.00	0.00	0.00	0.00
May	1978.12	0.00	1139.60	0.00	195.96	76.00	0.00	1316.98	0.00	0.00	0.00	0.00	0.00
June	1747.50	0.00	1064.00	0.00	171.82	62.20	0.00	1012.23	0.00	0.00	0.00	0.00	0.00
July	1978.12	0.00	1139.60	0.00	196.82	71.34	0.00	1149.01	0.00	0.00	0.00	0.00	0.00
August	1904.25	0.00	1122.40	0.00	188.49	66.40	0.00	1043.02	0.00	0.00	0.00	0.00	0.00
September	1821.37	0.00	1081.20	0.00	180.38	63.16	0.00	987.66	0.00	0.00	0.00	0.00	0.00
October	1978.12	0.00	1139.60	0.00	211.64	36.43	0.00	850.52	0.00	0.00	0.00	0.00	0.00
November	1821.37	0.00	1081.20	0.00	190.56	34.47	0.00	797.19	0.00	0.00	0.00	0.00	0.00
December	1904.25	0.00	1122.40	0.00	198.10	37.17	0.00	879.17	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	22566.37		13249.20		2297.66	643.31	0.00	12487.96
Minimum of Months	1729.50	0.00	1016.00	0.00	171.82	34.47	0.00	797.19	0.00	0.00	0.00	0.00	0.00
Maximum of Months	1978.12	0.00	1139.60	0.00	211.64	76.00	0.00	1316.98	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: END-USE ENERGY CONSUMPTION - NATURAL GAS
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	INTERIOREQUIPMENT:GAS []	EXTERIOREQUIPMENT:GAS []	HEATING:GAS [kWh]	COOLING:GAS []	WATERSYSTEMS:GAS []	COGENERATION:GAS [kWh]
January	0.00	0.00	517.23	0.00	0.00	3838.98
February	0.00	0.00	445.80	0.00	0.00	3466.56
March	0.00	0.00	437.79	0.00	0.00	3832.27
April	0.00	0.00	682.66	0.00	0.00	3716.03
May	0.00	0.00	746.72	0.00	0.00	3844.52
June	0.00	0.00	619.65	0.00	0.00	3755.85
July	0.00	0.00	725.42	0.00	0.00	3886.26
August	0.00	0.00	679.20	0.00	0.00	3890.34
September	0.00	0.00	653.39	0.00	0.00	3776.92
October	0.00	0.00	450.55	0.00	0.00	3890.29
November	0.00	0.00	442.16	0.00	0.00	3760.94
December	0.00	0.00	485.07	0.00	0.00	3853.33

Annual Sum or Average			6885.66			45512.30
Minimum of Months	0.00	0.00	437.79	0.00	0.00	3466.56
Maximum of Months	0.00	0.00	746.72	0.00	0.00	3890.34

Table of Contents
Report: PEAK ENERGY END-USE - ELECTRICITY PART 1
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	INTERIORLIGHTS:ELECTRICITY {Maximum}[W]	INTERIORLIGHTS:ELECTRICITY {TIMESTAMP}	EXTERIORLIGHTS:ELECTRICITY []	INTERIOREQUIPMENT:ELECTRICITY {Maximum}[W]	INTERIOREQUIPMENT:ELECTRICITY {TIMESTAMP}	EXTERIOREQUIPMENT:ELECTRICITY []	FANS:ELECTRICITY {Maximum}[W]	FANS:ELECTRICITY {TIMESTAMP}	PUMPS:ELECTRICITY {Maximum}[W]	PUMPS:ELECTRICITY {TIMESTAMP}	HEATING:ELECTRICITY {Maximum}[W]	HEATING:ELECTRICITY {TIMESTAMP}
January	7500.00	01-JAN-10:15	0.00	4500.00	01-JAN-09:15	0.00	808.58	31-JAN-14:00	178.97	22-JAN-17:00	0.00	01-JAN-00:15
February	7500.00	01-FEB-10:15	0.00	4500.00	01-FEB-09:15	0.00	831.06	27-FEB-14:00	190.94	22-FEB-15:00	0.00	01-FEB-00:15
March	7500.00	01-MAR-10:15	0.00	4500.00	01-MAR-09:15	0.00	853.80	22-MAR-10:00	189.67	22-MAR-15:45	0.00	01-MAR-00:15
April	7500.00	01-APR-10:15	0.00	4500.00	01-APR-09:15	0.00	703.50	12-APR-10:30	310.56	01-APR-06:45	0.00	01-APR-00:15
May	7500.00	01-MAY-10:15	0.00	4500.00	01-MAY-09:15	0.00	713.58	21-MAY-10:00	296.77	06-MAY-13:15	0.00	01-MAY-00:15
June	7500.00	03-JUN-10:15	0.00	4500.00	03-JUN-09:15	0.00	717.17	12-JUN-10:30	294.60	21-JUN-16:30	0.00	01-JUN-00:15
July	7500.00	01-JUL-10:15	0.00	4500.00	01-JUL-09:15	0.00	751.16	12-JUL-10:30	301.54	26-JUL-06:15	0.00	01-JUL-00:15
August	7500.00	01-AUG-10:15	0.00	4500.00	01-AUG-09:15	0.00	749.73	01-AUG-10:30	292.53	13-AUG-06:15	0.00	01-AUG-00:15
September	7500.00	02-SEP-10:15	0.00	4500.00	02-SEP-09:15	0.00	698.00	02-SEP-10:45	286.24	24-SEP-16:30	0.00	01-SEP-00:15
October	7500.00	01-OCT-10:15	0.00	4500.00	01-OCT-09:15	0.00	826.07	11-OCT-14:00	157.57	17-OCT-16:00	0.00	01-OCT-00:15
November	7500.00	01-NOV-10:15	0.00	4500.00	01-NOV-09:15	0.00	820.03	13-NOV-15:00	170.36	19-NOV-17:00	0.00	01-NOV-00:15
December	7500.00	02-DEC-10:15	0.00	4500.00	02-DEC-09:15	0.00	800.15	12-DEC-14:00	169.46	16-DEC-15:00	0.00	01-DEC-00:15

Annual Sum or Average
Minimum of Months	7500.00		0.00	4500.00		0.00	698.00		157.57		0.00
Maximum of Months	7500.00		0.00	4500.00		0.00	853.80		310.56		0.00

Table of Contents
Report: PEAK ENERGY END-USE - ELECTRICITY PART 2
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	COOLING:ELECTRICITY {Maximum}[W]	COOLING:ELECTRICITY {TIMESTAMP}	HEATREJECTION:ELECTRICITY []	HUMIDIFIER:ELECTRICITY []	HEATRECOVERY:ELECTRICITY []	WATERSYSTEMS:ELECTRICITY []	COGENERATION:ELECTRICITY []
January	5713.49	22-JAN-14:00	0.00	0.00	0.00	0.00	0.00
February	7499.95	22-FEB-15:00	0.00	0.00	0.00	0.00	0.00
March	7086.84	22-MAR-10:00	0.00	0.00	0.00	0.00	0.00
April	7363.25	11-APR-15:00	0.00	0.00	0.00	0.00	0.00
May	6945.70	06-MAY-13:00	0.00	0.00	0.00	0.00	0.00
June	6462.11	19-JUN-14:00	0.00	0.00	0.00	0.00	0.00
July	6002.62	29-JUL-14:00	0.00	0.00	0.00	0.00	0.00
August	5560.35	28-AUG-15:00	0.00	0.00	0.00	0.00	0.00
September	5834.48	24-SEP-14:00	0.00	0.00	0.00	0.00	0.00
October	5060.22	11-OCT-14:00	0.00	0.00	0.00	0.00	0.00
November	5141.55	19-NOV-15:00	0.00	0.00	0.00	0.00	0.00
December	5479.38	16-DEC-15:00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average
Minimum of Months	5060.22		0.00	0.00	0.00	0.00	0.00
Maximum of Months	7499.95		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: ELECTRIC COMPONENTS OF PEAK DEMAND
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ELECTRICITY:FACILITY {Maximum}[W]	ELECTRICITY:FACILITY {TIMESTAMP}	INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W]	INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W]	EXTERIORLIGHTS:ELECTRICITY []	EXTERIOREQUIPMENT:ELECTRICITY []	FANS:ELECTRICITY {AT MAX/MIN} [W]	PUMPS:ELECTRICITY {AT MAX/MIN} [W]	HEATING:ELECTRICITY {AT MAX/MIN} [W]	COOLING:ELECTRICITY {AT MAX/MIN} [W]	HEATREJECTION:ELECTRICITY []
January	18092.27	21-JAN-10:00	7500.00	4500.00	0.00	0.00	739.29	151.73	0.00	5201.25	0.00
February	19431.05	22-FEB-15:00	7500.00	3500.00	0.00	0.00	740.15	190.94	0.00	7499.95	0.00
March	20112.67	22-MAR-10:00	7500.00	4500.00	0.00	0.00	853.80	172.04	0.00	7086.84	0.00
April	19772.28	11-APR-14:00	7500.00	4000.00	0.00	0.00	619.31	292.80	0.00	7360.16	0.00
May	19267.76	06-MAY-10:00	7500.00	4500.00	0.00	0.00	623.14	290.01	0.00	6354.60	0.00
June	18884.57	19-JUN-14:00	7500.00	4000.00	0.00	0.00	635.67	286.79	0.00	6462.11	0.00
July	18428.18	29-JUL-14:00	7500.00	4000.00	0.00	0.00	657.30	268.26	0.00	6002.62	0.00
August	18435.29	01-AUG-10:00	7500.00	4500.00	0.00	0.00	734.72	232.72	0.00	5467.85	0.00
September	18469.92	04-SEP-10:00	7500.00	4500.00	0.00	0.00	679.65	248.40	0.00	5541.87	0.00
October	17526.28	11-OCT-14:00	7500.00	4000.00	0.00	0.00	826.07	139.99	0.00	5060.22	0.00
November	17577.38	11-NOV-14:00	7500.00	4000.00	0.00	0.00	810.68	141.13	0.00	5125.57	0.00
December	17753.05	19-DEC-14:00	7500.00	4000.00	0.00	0.00	709.36	161.40	0.00	5382.29	0.00

Annual Sum or Average
Minimum of Months	17526.28		7500.00	3500.00	0.00	0.00	619.31	139.99	0.00	5060.22	0.00
Maximum of Months	20112.67		7500.00	4500.00	0.00	0.00	853.80	292.80	0.00	7499.95	0.00

Table of Contents
Report: PEAK ENERGY END-USE - NATURAL GAS
For: Meter
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	INTERIOREQUIPMENT:GAS []	EXTERIOREQUIPMENT:GAS []	HEATING:GAS {Maximum}[W]	HEATING:GAS {TIMESTAMP}	COOLING:GAS []	WATERSYSTEMS:GAS []	COGENERATION:GAS {Maximum}[W]	COGENERATION:GAS {TIMESTAMP}
January	0.00	0.00	24748.86	16-JAN-06:15	0.00	0.00	5377.52	24-JAN-05:00
February	0.00	0.00	24877.18	15-FEB-06:15	0.00	0.00	5374.20	09-FEB-05:00
March	0.00	0.00	19226.72	05-MAR-06:15	0.00	0.00	5354.27	09-MAR-05:00
April	0.00	0.00	21516.42	30-APR-06:15	0.00	0.00	5357.59	30-APR-05:00
May	0.00	0.00	24865.83	10-MAY-06:15	0.00	0.00	5370.87	10-MAY-05:00
June	0.00	0.00	25256.88	04-JUN-06:15	0.00	0.00	5424.22	09-JUN-05:00
July	0.00	0.00	25562.40	16-JUL-06:15	0.00	0.00	5434.26	16-JUL-05:00
August	0.00	0.00	24591.67	05-AUG-06:15	0.00	0.00	5461.11	05-AUG-05:00
September	0.00	0.00	25979.51	12-SEP-06:15	0.00	0.00	5467.84	12-SEP-05:00
October	0.00	0.00	22124.45	02-OCT-06:15	0.00	0.00	5454.39	02-OCT-05:00
November	0.00	0.00	22368.84	15-NOV-06:15	0.00	0.00	5461.11	15-NOV-05:00
December	0.00	0.00	21731.02	13-DEC-06:15	0.00	0.00	5397.50	28-DEC-05:00

Annual Sum or Average
Minimum of Months	0.00	0.00	19226.72		0.00	0.00	5354.27
Maximum of Months	0.00	0.00	25979.51		0.00	0.00	5467.84

Table of Contents
Report: SETPOINTS NOT MET WITH TEMPERATURES
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE HEATING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE HEATING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00		0.00		0.00		0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: SETPOINTS NOT MET WITH TEMPERATURES
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE HEATING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE HEATING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.00	0.00	0.00	0.00	12.75	24.42	12.75	24.42
February	0.00	0.00	0.00	0.00	3.00	24.21	3.00	24.21
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	3.00	24.16	3.00	24.16
November	0.00	0.00	0.00	0.00	14.25	24.32	14.25	24.32
December	0.00	0.00	0.00	0.00	21.75	24.68	21.75	24.68

Annual Sum or Average	0.00		0.00		54.75	24.47	54.75	24.47
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	21.75	24.68	21.75	24.68

Table of Contents
Report: SETPOINTS NOT MET WITH TEMPERATURES
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE HEATING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE HEATING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.00	0.00	0.00	0.00	50.75	26.67	35.25	25.03
February	0.00	0.00	0.00	0.00	29.75	25.19	27.25	24.77
March	0.00	0.00	0.00	0.00	27.25	25.53	24.00	24.90
April	0.00	0.00	0.00	0.00	1.25	29.83	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	48.75	25.06	46.50	24.80
November	0.00	0.00	0.00	0.00	42.75	25.10	42.75	25.10
December	0.00	0.00	0.00	0.00	48.00	25.63	42.50	25.06

Annual Sum or Average	0.00		0.00		248.50	25.59	218.25	24.95
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	50.75	29.83	46.50	25.10

Table of Contents
Report: SETPOINTS NOT MET WITH TEMPERATURES
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE HEATING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE HEATING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	6.50	29.99	0.00	0.00
June	0.00	0.00	0.00	0.00	6.25	30.17	0.00	0.00
July	0.00	0.00	0.00	0.00	5.25	30.17	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00		0.00		18.00	30.11	0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	6.50	30.17	0.00	0.00

Table of Contents
Report: SETPOINTS NOT MET WITH TEMPERATURES
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE HEATING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE HEATING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.00	0.00	0.00	0.00	1.75	29.73	0.00	0.00
February	0.00	0.00	0.00	0.00	1.75	30.05	0.00	0.00
March	0.00	0.00	0.00	0.00	13.50	30.55	0.00	0.00
April	0.00	0.00	0.00	0.00	7.50	31.66	0.00	0.00
May	0.00	0.00	0.00	0.00	25.00	31.74	0.00	0.00
June	0.00	0.00	0.00	0.00	12.00	31.92	0.00	0.00
July	0.00	0.00	0.00	0.00	11.75	31.61	0.00	0.00
August	0.00	0.00	0.00	0.00	9.25	31.32	0.00	0.00
September	0.00	0.00	0.00	0.00	14.75	30.96	0.00	0.00
October	0.00	0.00	0.00	0.00	4.75	30.20	0.00	0.00
November	0.00	0.00	0.00	0.00	0.50	29.63	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00		0.00		102.50	31.29	0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	25.00	31.92	0.00	0.00

Table of Contents
Report: SETPOINTS NOT MET WITH TEMPERATURES
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE HEATING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE HEATING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE COOLING SETPOINT NOT MET WHILE OCCUPIED TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.25	21.97	0.00	0.00	0.00	0.00	0.00	0.00
February	0.25	21.97	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.50	21.97	0.00		0.00		0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.25	21.97	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COMFORT REPORT - SIMPLE 55
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER OR WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00		0.00		0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COMFORT REPORT - SIMPLE 55
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER OR WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	235.75	23.74	238.00	23.82	221.50	23.82
February	204.25	23.72	208.50	23.80	192.75	23.79
March	219.75	23.73	219.50	23.80	208.25	23.79
April	67.25	22.91	112.25	23.90	0.00	0.00
May	93.00	22.97	82.25	23.90	0.00	0.00
June	60.00	22.83	90.50	23.90	0.00	0.00
July	79.75	22.91	101.75	23.90	0.00	0.00
August	68.00	22.89	108.00	23.90	0.00	0.00
September	70.75	22.97	125.50	23.90	0.00	0.00
October	196.50	23.71	232.00	23.82	180.25	23.80
November	145.50	23.64	197.00	23.84	126.50	23.76
December	182.00	23.74	225.75	23.88	167.50	23.84

Annual Sum or Average	1622.50	23.50	1941.00	23.85	1096.75	23.80
Minimum of Months	60.00	22.83	82.25	23.80	0.00	0.00
Maximum of Months	235.75	23.74	238.00	23.90	221.50	23.84

Table of Contents
Report: COMFORT REPORT - SIMPLE 55
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER OR WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	201.75	23.83	245.00	23.93	194.50	23.88
February	170.00	23.80	211.75	23.91	162.50	23.85
March	190.00	23.84	223.25	23.90	183.00	23.89
April	51.75	22.73	161.75	23.90	0.00	0.00
May	82.50	22.79	132.00	23.90	0.00	0.00
June	45.75	22.72	148.75	23.90	0.00	0.00
July	59.25	22.77	153.25	23.90	0.00	0.00
August	51.25	22.74	164.75	23.90	0.00	0.00
September	53.25	22.79	156.75	23.90	0.00	0.00
October	157.75	23.88	245.75	23.98	152.50	23.92
November	130.50	23.88	215.25	24.04	121.00	23.96
December	160.75	23.87	232.50	23.99	153.00	23.93

Annual Sum or Average	1354.50	23.57	2290.75	23.93	966.50	23.90
Minimum of Months	45.75	22.72	132.00	23.90	0.00	0.00
Maximum of Months	201.75	23.88	245.75	24.04	194.50	23.96

Table of Contents
Report: COMFORT REPORT - SIMPLE 55
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER OR WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	228.75	23.25	217.50	23.46	195.00	23.41
February	194.50	23.35	189.25	23.58	165.00	23.53
March	196.50	23.41	203.75	23.61	172.00	23.56
April	110.50	22.42	94.00	23.77	0.00	0.00
May	150.00	22.41	80.75	23.82	0.00	0.00
June	86.75	22.44	113.25	23.83	0.00	0.00
July	112.75	22.39	119.50	23.82	0.00	0.00
August	110.25	22.43	94.25	23.77	0.00	0.00
September	113.00	22.39	75.25	23.74	0.00	0.00
October	189.00	23.35	211.75	23.64	152.50	23.56
November	153.00	23.12	170.25	23.53	109.75	23.35
December	185.50	23.15	195.00	23.47	145.75	23.35

Annual Sum or Average	1830.50	22.95	1764.50	23.63	940.00	23.47
Minimum of Months	86.75	22.39	75.25	23.46	0.00	0.00
Maximum of Months	228.75	23.41	217.50	23.83	195.00	23.56

Table of Contents
Report: COMFORT REPORT - SIMPLE 55
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER OR WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	192.75	22.77	172.50	23.15	128.50	22.97
February	165.50	22.88	157.50	23.32	109.50	23.16
March	182.75	22.94	169.75	23.30	129.25	23.18
April	164.75	22.25	60.75	23.74	0.00	0.00
May	186.50	22.23	56.50	23.79	0.00	0.00
June	139.25	22.26	66.50	23.76	0.00	0.00
July	170.75	22.25	65.75	23.75	0.00	0.00
August	159.00	22.25	70.00	23.72	0.00	0.00
September	147.50	22.25	72.50	23.74	0.00	0.00
October	141.75	22.75	171.00	23.44	76.00	23.06
November	157.00	22.71	142.50	23.26	84.75	22.90
December	158.75	22.69	150.75	23.24	89.50	22.91

Annual Sum or Average	1966.25	22.52	1356.00	23.42	617.50	23.04
Minimum of Months	139.25	22.23	56.50	23.15	0.00	0.00
Maximum of Months	192.75	22.94	172.50	23.79	129.25	23.18

Table of Contents
Report: COMFORT REPORT - SIMPLE 55
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]	ZONE THERMAL COMFORT ASHRAE 55 SIMPLE MODEL SUMMER OR WINTER CLOTHES NOT COMFORTABLE TIME {HOURS NON-ZERO} [HOURS]	ZONE MEAN AIR TEMPERATURE {FOR HOURS SHOWN} [C]
January	253.00	23.74	240.50	23.79	240.50	23.79
February	220.00	23.74	209.75	23.79	209.75	23.79
March	231.00	23.75	221.00	23.80	221.00	23.80
April	144.50	23.54	0.25	23.39	0.25	23.39
May	153.75	23.55	3.25	23.63	3.25	23.63
June	97.75	23.46	0.00	0.00	0.00	0.00
July	108.75	23.45	0.00	0.00	0.00	0.00
August	99.00	23.47	0.00	0.00	0.00	0.00
September	91.25	23.45	0.50	23.41	0.50	23.41
October	235.00	23.77	214.50	23.83	214.25	23.83
November	185.50	23.73	139.25	23.79	138.75	23.79
December	224.00	23.74	209.00	23.80	209.00	23.80

Annual Sum or Average	2043.50	23.66	1238.00	23.80	1237.25	23.80
Minimum of Months	91.25	23.45	0.00	0.00	0.00	0.00
Maximum of Months	253.00	23.77	240.50	23.83	240.50	23.83

Table of Contents
Report: OCCUPANT COMFORT DATA SUMMARY
For: SPACE1-1 PEOPLE 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PEOPLE OCCUPANT COUNT {HOURS NON-ZERO} [HOURS]	PEOPLE AIR TEMPERATURE {FOR HOURS SHOWN} [C]	PEOPLE AIR RELATIVE HUMIDITY {FOR HOURS SHOWN} [%]	ZONE THERMAL COMFORT FANGER MODEL PMV []	ZONE THERMAL COMFORT FANGER MODEL PPD []
January	253.00000	0.00000	0.00000	0.00000	0.00000
February	220.00000	0.00000	0.00000	0.00000	0.00000
March	231.00000	0.00000	0.00000	0.00000	0.00000
April	242.00000	0.00000	0.00000	0.00000	0.00000
May	253.00000	0.00000	0.00000	0.00000	0.00000
June	220.00000	0.00000	0.00000	0.00000	0.00000
July	253.00000	0.00000	0.00000	0.00000	0.00000
August	242.00000	0.00000	0.00000	0.00000	0.00000
September	231.00000	0.00000	0.00000	0.00000	0.00000
October	253.00000	0.00000	0.00000	0.00000	0.00000
November	231.00000	0.00000	0.00000	0.00000	0.00000
December	242.00000	0.00000	0.00000	0.00000	0.00000

Annual Sum or Average	2871.00000	0.00000	0.00000
Minimum of Months	220.00000	0.00000	0.00000	0.00000	0.00000
Maximum of Months	253.00000	0.00000	0.00000	0.00000	0.00000

Table of Contents
Report: OCCUPANT COMFORT DATA SUMMARY
For: SPACE2-1 PEOPLE 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PEOPLE OCCUPANT COUNT {HOURS NON-ZERO} [HOURS]	PEOPLE AIR TEMPERATURE {FOR HOURS SHOWN} [C]	PEOPLE AIR RELATIVE HUMIDITY {FOR HOURS SHOWN} [%]	ZONE THERMAL COMFORT FANGER MODEL PMV []	ZONE THERMAL COMFORT FANGER MODEL PPD []
January	253.00000	0.00000	0.00000	0.00000	0.00000
February	220.00000	0.00000	0.00000	0.00000	0.00000
March	231.00000	0.00000	0.00000	0.00000	0.00000
April	242.00000	0.00000	0.00000	0.00000	0.00000
May	253.00000	0.00000	0.00000	0.00000	0.00000
June	220.00000	0.00000	0.00000	0.00000	0.00000
July	253.00000	0.00000	0.00000	0.00000	0.00000
August	242.00000	0.00000	0.00000	0.00000	0.00000
September	231.00000	0.00000	0.00000	0.00000	0.00000
October	253.00000	0.00000	0.00000	0.00000	0.00000
November	231.00000	0.00000	0.00000	0.00000	0.00000
December	242.00000	0.00000	0.00000	0.00000	0.00000

Annual Sum or Average	2871.00000	0.00000	0.00000
Minimum of Months	220.00000	0.00000	0.00000	0.00000	0.00000
Maximum of Months	253.00000	0.00000	0.00000	0.00000	0.00000

Table of Contents
Report: OCCUPANT COMFORT DATA SUMMARY
For: SPACE3-1 PEOPLE 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PEOPLE OCCUPANT COUNT {HOURS NON-ZERO} [HOURS]	PEOPLE AIR TEMPERATURE {FOR HOURS SHOWN} [C]	PEOPLE AIR RELATIVE HUMIDITY {FOR HOURS SHOWN} [%]	ZONE THERMAL COMFORT FANGER MODEL PMV []	ZONE THERMAL COMFORT FANGER MODEL PPD []
January	253.00000	0.00000	0.00000	0.00000	0.00000
February	220.00000	0.00000	0.00000	0.00000	0.00000
March	231.00000	0.00000	0.00000	0.00000	0.00000
April	242.00000	0.00000	0.00000	0.00000	0.00000
May	253.00000	0.00000	0.00000	0.00000	0.00000
June	220.00000	0.00000	0.00000	0.00000	0.00000
July	253.00000	0.00000	0.00000	0.00000	0.00000
August	242.00000	0.00000	0.00000	0.00000	0.00000
September	231.00000	0.00000	0.00000	0.00000	0.00000
October	253.00000	0.00000	0.00000	0.00000	0.00000
November	231.00000	0.00000	0.00000	0.00000	0.00000
December	242.00000	0.00000	0.00000	0.00000	0.00000

Annual Sum or Average	2871.00000	0.00000	0.00000
Minimum of Months	220.00000	0.00000	0.00000	0.00000	0.00000
Maximum of Months	253.00000	0.00000	0.00000	0.00000	0.00000

Table of Contents
Report: OCCUPANT COMFORT DATA SUMMARY
For: SPACE4-1 PEOPLE 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PEOPLE OCCUPANT COUNT {HOURS NON-ZERO} [HOURS]	PEOPLE AIR TEMPERATURE {FOR HOURS SHOWN} [C]	PEOPLE AIR RELATIVE HUMIDITY {FOR HOURS SHOWN} [%]	ZONE THERMAL COMFORT FANGER MODEL PMV []	ZONE THERMAL COMFORT FANGER MODEL PPD []
January	253.00000	0.00000	0.00000	0.00000	0.00000
February	220.00000	0.00000	0.00000	0.00000	0.00000
March	231.00000	0.00000	0.00000	0.00000	0.00000
April	242.00000	0.00000	0.00000	0.00000	0.00000
May	253.00000	0.00000	0.00000	0.00000	0.00000
June	220.00000	0.00000	0.00000	0.00000	0.00000
July	253.00000	0.00000	0.00000	0.00000	0.00000
August	242.00000	0.00000	0.00000	0.00000	0.00000
September	231.00000	0.00000	0.00000	0.00000	0.00000
October	253.00000	0.00000	0.00000	0.00000	0.00000
November	231.00000	0.00000	0.00000	0.00000	0.00000
December	242.00000	0.00000	0.00000	0.00000	0.00000

Annual Sum or Average	2871.00000	0.00000	0.00000
Minimum of Months	220.00000	0.00000	0.00000	0.00000	0.00000
Maximum of Months	253.00000	0.00000	0.00000	0.00000	0.00000

Table of Contents
Report: OCCUPANT COMFORT DATA SUMMARY
For: SPACE5-1 PEOPLE 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PEOPLE OCCUPANT COUNT {HOURS NON-ZERO} [HOURS]	PEOPLE AIR TEMPERATURE {FOR HOURS SHOWN} [C]	PEOPLE AIR RELATIVE HUMIDITY {FOR HOURS SHOWN} [%]	ZONE THERMAL COMFORT FANGER MODEL PMV []	ZONE THERMAL COMFORT FANGER MODEL PPD []
January	253.00000	0.00000	0.00000	0.00000	0.00000
February	220.00000	0.00000	0.00000	0.00000	0.00000
March	231.00000	0.00000	0.00000	0.00000	0.00000
April	242.00000	0.00000	0.00000	0.00000	0.00000
May	253.00000	0.00000	0.00000	0.00000	0.00000
June	220.00000	0.00000	0.00000	0.00000	0.00000
July	253.00000	0.00000	0.00000	0.00000	0.00000
August	242.00000	0.00000	0.00000	0.00000	0.00000
September	231.00000	0.00000	0.00000	0.00000	0.00000
October	253.00000	0.00000	0.00000	0.00000	0.00000
November	231.00000	0.00000	0.00000	0.00000	0.00000
December	242.00000	0.00000	0.00000	0.00000	0.00000

Annual Sum or Average	2871.00000	0.00000	0.00000
Minimum of Months	220.00000	0.00000	0.00000	0.00000	0.00000
Maximum of Months	253.00000	0.00000	0.00000	0.00000	0.00000

Table of Contents
Report: CHILLER REPORT
For: CENTRAL CHILLER
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	CHILLER ELECTRIC ENERGY [kWh]	CHILLER ELECTRIC POWER {Maximum}[W]	CHILLER ELECTRIC POWER {TIMESTAMP}	CHILLER ELECTRIC ENERGY {HOURS NON-ZERO} [HOURS]	CHILLER EVAPORATOR COOLING ENERGY [kWh]	CHILLER CONDENSER HEAT TRANSFER ENERGY [kWh]	CHILLER COP [W/W]	CHILLER COP {MINIMUM}[W/W]	CHILLER COP {TIMESTAMP}	CHILLER COP {Maximum}[W/W]	CHILLER COP {TIMESTAMP}
January	1052.10	5713.49	22-JAN-15:00	322.00	4336.70	5388.80	1.77	0.00	01-JAN-00:15	4.30	09-JAN-06:13
February	966.22	7499.95	22-FEB-16:00	280.00	3971.46	4937.68	1.71	0.00	01-FEB-00:15	4.30	25-FEB-06:12
March	1127.13	7086.84	22-MAR-11:00	294.00	4655.55	5782.68	1.63	0.00	01-MAR-00:15	4.29	07-MAR-06:15
April	1306.72	7363.25	11-APR-16:00	308.00	5419.54	6726.26	1.78	0.00	01-APR-00:15	4.41	24-APR-06:03
May	1316.98	6945.70	06-MAY-14:00	322.00	5478.18	6795.15	1.81	0.00	01-MAY-00:15	4.40	10-MAY-06:05
June	1012.23	6462.11	19-JUN-15:00	280.00	4244.30	5256.52	1.63	0.00	01-JUN-00:15	4.39	11-JUN-06:03
July	1149.01	6002.62	29-JUL-15:00	322.00	4824.95	5973.96	1.82	0.00	01-JUL-00:15	4.40	12-JUL-06:03
August	1043.02	5560.35	28-AUG-16:00	308.00	4380.67	5423.69	1.73	0.00	01-AUG-00:15	4.41	01-AUG-06:03
September	987.66	5834.48	24-SEP-15:00	294.00	4148.96	5136.62	1.71	0.00	01-SEP-00:15	4.42	13-SEP-06:03
October	850.52	5060.22	11-OCT-15:00	322.00	3491.00	4341.52	1.74	0.00	01-OCT-00:15	4.31	24-OCT-11:00
November	797.19	5141.55	19-NOV-16:00	294.00	3269.37	4066.55	1.63	0.00	01-NOV-00:15	4.30	25-NOV-14:00
December	879.17	5479.38	16-DEC-16:00	308.00	3600.17	4479.34	1.68	0.00	01-DEC-00:15	4.26	19-DEC-06:15

Annual Sum or Average	12487.96			3654.00	51820.83	64308.78	1.72
Minimum of Months	797.19	5060.22		280.00	3269.37	4066.55	1.63	0.00		4.26
Maximum of Months	1316.98	7499.95		322.00	5478.18	6795.15	1.82	0.00		4.42

Table of Contents
Report: BOILER REPORT
For: CENTRAL BOILER
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	BOILER HEATING ENERGY [kWh]	BOILER GAS ENERGY [kWh]	BOILER HEATING ENERGY {HOURS NON-ZERO} [HOURS]	BOILER HEATING RATE {Maximum}[W]	BOILER HEATING RATE {TIMESTAMP}	BOILER GAS RATE {Maximum}[W]	BOILER GAS RATE {TIMESTAMP}	BOILER INLET TEMPERATURE [C]	BOILER OUTLET TEMPERATURE [C]	BOILER MASS FLOW RATE [kg/s]	BOILER ANCILLARY ELECTRIC POWER [W]
January	413.79	517.23	122.37	48308.48	03-JAN-06:03	60385.60	03-JAN-06:03	45.55	51.07	0.00	0.00
February	356.64	445.80	100.87	48308.48	01-FEB-06:03	60385.60	01-FEB-06:03	45.72	50.73	0.00	0.00
March	350.23	437.79	107.37	48308.48	01-MAR-06:03	60385.60	01-MAR-06:03	45.09	49.98	0.00	0.00
April	546.13	682.66	195.75	48308.48	02-APR-06:03	60385.60	02-APR-06:03	44.86	54.50	0.01	0.00
May	597.38	746.72	227.25	48308.48	01-MAY-06:03	60385.60	01-MAY-06:03	44.61	55.73	0.01	0.00
June	495.72	619.65	169.38	48308.48	03-JUN-06:03	60385.60	03-JUN-06:03	45.03	53.26	0.01	0.00
July	580.34	725.42	208.75	48308.48	01-JUL-06:03	60385.60	01-JUL-06:03	45.05	55.01	0.01	0.00
August	543.36	679.20	191.25	48308.48	01-AUG-06:03	60385.60	01-AUG-06:03	44.82	53.94	0.01	0.00
September	522.71	653.39	186.25	48308.48	03-SEP-06:03	60385.60	03-SEP-06:03	44.89	54.11	0.01	0.00
October	360.44	450.55	116.50	48308.48	01-OCT-06:03	60385.60	01-OCT-06:03	45.18	50.53	0.00	0.00
November	353.73	442.16	115.37	48308.48	01-NOV-06:02	60385.60	01-NOV-06:02	45.30	50.75	0.00	0.00
December	388.06	485.07	119.88	48308.48	02-DEC-06:03	60385.60	02-DEC-06:03	45.34	50.80	0.00	0.00

Annual Sum or Average	5508.53	6885.66	1861.00					45.12	52.54	0.00	0.00
Minimum of Months	350.23	437.79	100.87	48308.48		60385.60		44.61	49.98	0.00	0.00
Maximum of Months	597.38	746.72	227.25	48308.48		60385.60		45.72	55.73	0.01	0.00

Table of Contents
Report: DX REPORT
For: MAIN COOLING COIL 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	COOLING COIL TOTAL COOLING ENERGY [kWh]	COOLING COIL ELECTRIC ENERGY []	COOLING COIL TOTAL COOLING ENERGY {HOURS NON-ZERO} [HOURS]	COOLING COIL SENSIBLE COOLING ENERGY [kWh]	COOLING COIL LATENT COOLING ENERGY []	COOLING COIL CRANKCASE HEATER ELECTRIC ENERGY []	COOLING COIL RUNTIME FRACTION []	COOLING COIL RUNTIME FRACTION []	COOLING COIL TOTAL COOLING RATE {Maximum}[W]	COOLING COIL TOTAL COOLING RATE {TIMESTAMP}	COOLING COIL SENSIBLE COOLING RATE {Maximum}[W]	COOLING COIL SENSIBLE COOLING RATE {TIMESTAMP}	COOLING COIL LATENT COOLING RATE []	COOLING COIL ELECTRIC POWER []	COOLING COIL CRANKCASE HEATER ELECTRIC POWER []
January	4307.95	0.00	322.00	2921.71	0.00	0.00	0.00	0.00	23070.66	22-JAN-15:00	17306.63	31-JAN-15:00	0.00	0.00	0.00
February	3946.41	0.00	280.00	2597.40	0.00	0.00	0.00	0.00	28735.41	22-FEB-16:00	18029.45	27-FEB-15:00	0.00	0.00	0.00
March	4628.45	0.00	294.00	2750.38	0.00	0.00	0.00	0.00	27678.94	22-MAR-11:00	16649.40	21-MAR-14:45	0.00	0.00	0.00
April	5356.64	0.00	308.00	3290.20	0.00	0.00	0.00	0.00	27696.08	11-APR-15:00	17361.30	08-APR-15:00	0.00	0.00	0.00
May	5418.21	0.00	322.00	3356.82	0.00	0.00	0.00	0.00	27172.92	06-MAY-14:00	18461.27	20-MAY-15:00	0.00	0.00	0.00
June	4195.00	0.00	280.00	2808.46	0.00	0.00	0.00	0.00	25671.16	19-JUN-15:00	16725.30	25-JUN-15:00	0.00	0.00	0.00
July	4768.30	0.00	322.00	3144.03	0.00	0.00	0.00	0.00	23893.63	29-JUL-15:00	15996.74	22-JUL-15:00	0.00	0.00	0.00
August	4327.69	0.00	308.00	2979.02	0.00	0.00	0.00	0.00	22883.78	28-AUG-16:00	16937.29	19-AUG-15:00	0.00	0.00	0.00
September	4098.53	0.00	294.00	2845.59	0.00	0.00	0.00	0.00	23779.00	24-SEP-15:00	16476.33	05-SEP-16:00	0.00	0.00	0.00
October	3465.64	0.00	322.00	2789.08	0.00	0.00	0.00	0.00	20237.56	11-OCT-15:00	17200.49	11-OCT-15:00	0.00	0.00	0.00
November	3245.14	0.00	294.00	2521.45	0.00	0.00	0.00	0.00	20947.92	19-NOV-16:00	16485.46	07-NOV-15:00	0.00	0.00	0.00
December	3574.35	0.00	308.00	2774.40	0.00	0.00	0.00	0.00	22108.80	16-DEC-16:00	17337.01	18-DEC-15:00	0.00	0.00	0.00

Annual Sum or Average	51332.32		3654.00	34778.54
Minimum of Months	3245.14	0.00	280.00	2521.45	0.00	0.00	0.00	0.00	20237.56		15996.74		0.00	0.00	0.00
Maximum of Months	5418.21	0.00	322.00	3356.82	0.00	0.00	0.00	0.00	28735.41		18461.27		0.00	0.00	0.00

Table of Contents
Report: WINDOW REPORT
For: WF-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	SURFACE WINDOW HEAT GAIN RATE [W]	SURFACE WINDOW HEAT LOSS RATE [W]	SURFACE WINDOW INSIDE FACE GLAZING CONDENSATION STATUS {HOURS NON-ZERO} [HOURS]	SURFACE SHADING DEVICE IS ON TIME FRACTION {HOURS NON-ZERO} [HOURS]	SURFACE STORM WINDOW ON OFF STATUS {HOURS NON-ZERO} [HOURS]
January	479.22	100.86	378.37	598.97	7.94	0.00	0.00	744.00
February	418.47	36.64	381.83	541.60	6.78	0.00	0.00	672.00
March	414.09	18.90	395.19	536.35	4.00	0.00	0.00	744.00
April	400.88	9.66	391.23	509.50	6.19	0.00	0.00	720.00
May	347.93	2.52	345.41	446.14	10.61	0.00	0.00	744.00
June	361.83	0.62	361.21	414.86	26.58	0.00	0.00	720.00
July	368.30	0.82	367.49	416.35	32.79	0.00	0.00	744.00
August	378.11	7.24	370.87	421.06	38.27	0.00	0.00	744.00
September	461.57	44.41	417.17	499.68	52.92	0.00	0.00	720.00
October	454.63	37.43	417.19	503.34	36.49	0.00	0.00	744.00
November	440.41	57.71	382.70	495.82	32.72	0.00	0.00	720.00
December	522.37	134.26	388.10	620.05	12.55	0.00	0.00	744.00

Annual Sum or Average	420.72	37.70	383.02	500.19	22.37	0.00	0.00	8760.00
Minimum of Months	347.93	0.62	345.41	414.86	4.00	0.00	0.00	672.00
Maximum of Months	522.37	134.26	417.19	620.05	52.92	0.00	0.00	744.00

Table of Contents
Report: WINDOW REPORT
For: DF-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	SURFACE WINDOW HEAT GAIN RATE [W]	SURFACE WINDOW HEAT LOSS RATE [W]	SURFACE WINDOW INSIDE FACE GLAZING CONDENSATION STATUS {HOURS NON-ZERO} [HOURS]	SURFACE SHADING DEVICE IS ON TIME FRACTION {HOURS NON-ZERO} [HOURS]	SURFACE STORM WINDOW ON OFF STATUS {HOURS NON-ZERO} [HOURS]
January	190.01	54.09	135.91	260.63	5.70	0.00	0.00	744.00
February	165.88	24.27	141.61	237.91	4.56	0.00	0.00	672.00
March	164.08	18.62	145.45	235.54	2.90	0.00	0.00	744.00
April	151.87	12.42	139.45	213.21	4.52	0.00	0.00	720.00
May	123.29	3.30	119.99	174.94	7.48	0.00	0.00	744.00
June	125.69	0.77	124.93	152.28	18.14	0.00	0.00	720.00
July	128.68	1.17	127.51	152.56	22.01	0.00	0.00	744.00
August	140.43	9.27	131.16	164.41	25.51	0.00	0.00	744.00
September	186.39	40.22	146.17	213.04	34.71	0.00	0.00	720.00
October	189.61	39.96	149.65	222.12	24.71	0.00	0.00	744.00
November	179.11	41.83	137.27	214.12	22.15	3.25	0.00	720.00
December	204.03	63.77	140.26	262.62	9.46	0.00	0.00	744.00

Annual Sum or Average	162.41	25.84	136.57	208.49	15.19	3.25	0.00	8760.00
Minimum of Months	123.29	0.77	119.99	152.28	2.90	0.00	0.00	672.00
Maximum of Months	204.03	63.77	149.65	262.62	34.71	3.25	0.00	744.00

Table of Contents
Report: WINDOW REPORT
For: WR-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	SURFACE WINDOW HEAT GAIN RATE [W]	SURFACE WINDOW HEAT LOSS RATE [W]	SURFACE WINDOW INSIDE FACE GLAZING CONDENSATION STATUS {HOURS NON-ZERO} [HOURS]	SURFACE SHADING DEVICE IS ON TIME FRACTION {HOURS NON-ZERO} [HOURS]	SURFACE STORM WINDOW ON OFF STATUS {HOURS NON-ZERO} [HOURS]
January	639.66	277.84	361.83	719.90	6.06	0.00	0.00	744.00
February	557.02	169.15	387.86	638.32	4.77	0.00	0.00	672.00
March	590.35	193.30	397.06	671.65	3.21	0.00	0.00	744.00
April	513.58	155.47	358.11	583.73	5.11	0.00	0.00	720.00
May	401.67	98.95	302.72	459.68	8.19	0.00	0.00	744.00
June	410.79	92.55	318.24	446.28	19.08	0.00	0.00	720.00
July	444.33	112.17	332.16	479.74	22.89	0.00	0.00	744.00
August	455.63	120.10	335.53	488.63	26.03	0.00	0.00	744.00
September	584.91	216.38	368.54	620.11	33.50	0.00	0.00	720.00
October	675.79	283.67	392.12	722.65	24.99	0.00	0.00	744.00
November	693.33	322.93	370.41	744.01	22.02	0.00	0.00	720.00
December	657.33	282.80	374.53	724.37	9.84	0.00	0.00	744.00

Annual Sum or Average	552.01	193.94	358.06	608.11	15.51	0.00	0.00	8760.00
Minimum of Months	401.67	92.55	302.72	446.28	3.21	0.00	0.00	672.00
Maximum of Months	693.33	322.93	397.06	744.01	33.50	0.00	0.00	744.00

Table of Contents
Report: WINDOW REPORT
For: WB-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	SURFACE WINDOW HEAT GAIN RATE [W]	SURFACE WINDOW HEAT LOSS RATE [W]	SURFACE WINDOW INSIDE FACE GLAZING CONDENSATION STATUS {HOURS NON-ZERO} [HOURS]	SURFACE SHADING DEVICE IS ON TIME FRACTION {HOURS NON-ZERO} [HOURS]	SURFACE STORM WINDOW ON OFF STATUS {HOURS NON-ZERO} [HOURS]
January	543.25	8.26	534.99	654.19	10.48	0.00	0.00	744.00
February	615.53	21.62	593.92	740.12	8.25	0.00	0.00	672.00
March	792.51	136.29	656.22	929.01	5.53	0.00	0.00	744.00
April	959.37	291.99	667.38	1096.82	8.83	0.00	0.00	720.00
May	1023.98	418.80	605.18	1156.77	14.47	0.00	0.00	744.00
June	1217.32	538.99	678.33	1319.29	33.53	0.00	0.00	720.00
July	1224.62	519.62	705.00	1322.42	40.40	0.00	0.00	744.00
August	981.51	330.06	651.44	1059.34	45.84	0.00	0.00	744.00
September	864.96	224.83	640.12	924.48	58.91	0.00	0.00	720.00
October	709.79	98.09	611.71	767.73	43.52	0.00	0.00	744.00
November	569.74	25.61	544.13	623.07	38.25	0.00	0.00	720.00
December	532.89	2.34	530.55	615.67	16.80	0.00	0.00	744.00

Annual Sum or Average	837.37	219.08	618.29	935.05	27.14	0.00	0.00	8760.00
Minimum of Months	532.89	2.34	530.55	615.67	5.53	0.00	0.00	672.00
Maximum of Months	1224.62	538.99	705.00	1322.42	58.91	0.00	0.00	744.00

Table of Contents
Report: WINDOW REPORT
For: DB-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	SURFACE WINDOW HEAT GAIN RATE [W]	SURFACE WINDOW HEAT LOSS RATE [W]	SURFACE WINDOW INSIDE FACE GLAZING CONDENSATION STATUS {HOURS NON-ZERO} [HOURS]	SURFACE SHADING DEVICE IS ON TIME FRACTION {HOURS NON-ZERO} [HOURS]	SURFACE STORM WINDOW ON OFF STATUS {HOURS NON-ZERO} [HOURS]
January	132.41	2.90	129.52	182.81	5.35	0.00	0.00	744.00
February	150.38	6.60	143.78	207.71	4.14	0.00	0.00	672.00
March	194.82	35.95	158.86	258.51	2.81	0.50	0.00	744.00
April	234.56	73.00	161.56	298.56	4.54	0.00	0.00	720.00
May	249.24	102.73	146.51	310.85	7.35	0.00	0.00	744.00
June	295.29	131.07	164.21	342.36	17.11	0.00	0.00	720.00
July	296.86	126.18	170.67	341.07	20.41	0.00	0.00	744.00
August	239.31	81.60	157.71	273.93	23.27	0.00	0.00	744.00
September	212.94	57.98	154.97	238.99	30.22	0.00	0.00	720.00
October	175.23	27.15	148.09	199.43	21.96	0.00	0.00	744.00
November	139.97	8.24	131.73	162.10	19.22	3.75	0.00	720.00
December	129.39	0.95	128.44	166.07	8.74	0.25	0.00	744.00

Annual Sum or Average	204.46	54.78	149.68	248.74	13.79	4.50	0.00	8760.00
Minimum of Months	129.39	0.95	128.44	162.10	2.81	0.00	0.00	672.00
Maximum of Months	296.86	131.07	170.67	342.36	30.22	3.75	0.00	744.00

Table of Contents
Report: WINDOW REPORT
For: WL-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION RATE [W]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	SURFACE WINDOW HEAT GAIN RATE [W]	SURFACE WINDOW HEAT LOSS RATE [W]	SURFACE WINDOW INSIDE FACE GLAZING CONDENSATION STATUS {HOURS NON-ZERO} [HOURS]	SURFACE SHADING DEVICE IS ON TIME FRACTION {HOURS NON-ZERO} [HOURS]	SURFACE STORM WINDOW ON OFF STATUS {HOURS NON-ZERO} [HOURS]
January	430.30	109.35	320.95	503.70	6.49	0.00	0.00	744.00
February	432.36	75.07	357.29	508.91	5.12	0.00	0.00	672.00
March	499.52	117.20	382.31	577.42	3.88	0.00	0.00	744.00
April	630.94	243.48	387.46	713.13	6.47	0.00	0.00	720.00
May	674.92	332.12	342.79	754.61	10.84	0.00	0.00	744.00
June	695.15	326.23	368.91	753.41	22.21	0.00	0.00	720.00
July	650.59	280.01	370.58	703.43	25.21	0.00	0.00	744.00
August	659.11	286.02	373.09	710.12	28.42	0.00	0.00	744.00
September	708.99	323.89	385.10	757.92	37.11	0.00	0.00	720.00
October	569.52	195.06	374.47	614.99	26.22	0.00	0.00	744.00
November	445.53	118.61	326.92	487.02	22.88	0.00	0.00	720.00
December	425.80	102.81	322.99	484.88	10.49	0.00	0.00	744.00

Annual Sum or Average	569.11	209.78	359.34	631.28	17.15	0.00	0.00	8760.00
Minimum of Months	425.80	75.07	320.95	484.88	3.88	0.00	0.00	672.00
Maximum of Months	708.99	332.12	387.46	757.92	37.11	0.00	0.00	744.00

Table of Contents
Report: WINDOW ENERGY REPORT
For: WF-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW HEAT GAIN ENERGY [kWh]	SURFACE WINDOW HEAT LOSS ENERGY [kWh]
January	356.54	75.04	281.51	445.63	5.91
February	281.21	24.62	256.59	363.95	4.56
March	308.08	14.06	294.02	399.05	2.98
April	288.64	6.95	281.68	366.84	4.46
May	258.86	1.88	256.98	331.93	7.90
June	260.52	0.45	260.07	298.70	19.14
July	274.02	0.61	273.41	309.76	24.40
August	281.32	5.39	275.93	313.27	28.47
September	332.33	31.97	300.36	359.77	38.10
October	338.24	27.85	310.39	374.48	27.14
November	317.10	41.55	275.55	356.99	23.56
December	388.64	99.89	288.75	461.32	9.33

Annual Sum or Average	3685.49	330.26	3355.24	4381.69	195.94
Minimum of Months	258.86	0.45	256.59	298.70	2.98
Maximum of Months	388.64	99.89	310.39	461.32	38.10

Table of Contents
Report: WINDOW ENERGY REPORT
For: DF-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW HEAT GAIN ENERGY [kWh]	SURFACE WINDOW HEAT LOSS ENERGY [kWh]
January	141.36	40.24	101.12	193.91	4.24
February	111.47	16.31	95.16	159.87	3.07
March	122.07	13.86	108.22	175.24	2.16
April	109.34	8.94	100.40	153.51	3.26
May	91.73	2.46	89.27	130.16	5.56
June	90.50	0.55	89.95	109.64	13.06
July	95.74	0.87	94.87	113.50	16.37
August	104.48	6.90	97.58	122.32	18.98
September	134.20	28.96	105.24	153.39	24.99
October	141.07	29.73	111.34	165.26	18.39
November	128.96	30.12	98.84	154.17	15.95
December	151.80	47.44	104.35	195.39	7.04

Annual Sum or Average	1422.72	226.37	1196.34	1826.37	133.07
Minimum of Months	90.50	0.55	89.27	109.64	2.16
Maximum of Months	151.80	47.44	111.34	195.39	24.99

Table of Contents
Report: WINDOW ENERGY REPORT
For: WR-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW HEAT GAIN ENERGY [kWh]	SURFACE WINDOW HEAT LOSS ENERGY [kWh]
January	475.91	206.71	269.20	535.61	4.51
February	374.31	113.67	260.64	428.95	3.21
March	439.22	143.81	295.41	499.70	2.39
April	369.78	111.94	257.84	420.29	3.68
May	298.84	73.62	225.22	342.00	6.10
June	295.77	66.64	229.13	321.32	13.73
July	330.58	83.45	247.13	356.93	17.03
August	338.99	89.35	249.64	363.54	19.37
September	421.14	155.79	265.35	446.48	24.12
October	502.79	211.05	291.74	537.65	18.59
November	499.20	232.51	266.69	535.69	15.85
December	489.05	210.40	278.65	538.93	7.32

Annual Sum or Average	4835.59	1698.95	3136.63	5327.08	135.90
Minimum of Months	295.77	66.64	225.22	321.32	2.39
Maximum of Months	502.79	232.51	295.41	538.93	24.12

Table of Contents
Report: WINDOW ENERGY REPORT
For: WB-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW HEAT GAIN ENERGY [kWh]	SURFACE WINDOW HEAT LOSS ENERGY [kWh]
January	404.18	6.14	398.03	486.72	7.80
February	413.64	14.53	399.11	497.36	5.54
March	589.63	101.40	488.23	691.18	4.11
April	690.74	210.23	480.51	789.71	6.36
May	761.84	311.59	450.25	860.63	10.76
June	876.47	388.08	488.39	949.89	24.14
July	911.12	386.59	524.52	983.88	30.06
August	730.24	245.57	484.67	788.15	34.10
September	622.77	161.88	460.89	665.63	42.42
October	528.08	72.98	455.11	571.19	32.38
November	410.21	18.44	391.78	448.61	27.54
December	396.47	1.74	394.73	458.06	12.50

Annual Sum or Average	7335.39	1919.16	5416.23	8191.01	237.70
Minimum of Months	396.47	1.74	391.78	448.61	4.11
Maximum of Months	911.12	388.08	524.52	983.88	42.42

Table of Contents
Report: WINDOW ENERGY REPORT
For: DB-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW HEAT GAIN ENERGY [kWh]	SURFACE WINDOW HEAT LOSS ENERGY [kWh]
January	98.52	2.16	96.36	136.01	3.98
February	101.05	4.43	96.62	139.58	2.78
March	144.94	26.75	118.19	192.33	2.09
April	168.88	52.56	116.33	214.97	3.27
May	185.43	76.43	109.00	231.28	5.47
June	212.61	94.37	118.23	246.50	12.32
July	220.86	93.88	126.98	253.75	15.19
August	178.04	60.71	117.33	203.80	17.31
September	153.32	41.74	111.58	172.07	21.76
October	130.37	20.20	110.18	148.38	16.34
November	100.78	5.93	94.84	116.71	13.84
December	96.26	0.70	95.56	123.56	6.50

Annual Sum or Average	1791.08	479.87	1311.21	2178.94	120.84
Minimum of Months	96.26	0.70	94.84	116.71	2.09
Maximum of Months	220.86	94.37	126.98	253.75	21.76

Table of Contents
Report: WINDOW ENERGY REPORT
For: WL-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SURFACE WINDOW TRANSMITTED SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	SURFACE WINDOW HEAT GAIN ENERGY [kWh]	SURFACE WINDOW HEAT LOSS ENERGY [kWh]
January	320.14	81.35	238.79	374.75	4.83
February	290.55	50.45	240.10	341.99	3.44
March	371.64	87.20	284.44	429.60	2.88
April	454.28	175.31	278.97	513.45	4.66
May	502.14	247.10	255.04	561.43	8.07
June	500.51	234.89	265.62	542.46	15.99
July	484.04	208.33	275.71	523.35	18.76
August	490.38	212.80	277.58	528.33	21.14
September	510.47	233.20	277.27	545.70	26.72
October	423.73	145.12	278.61	457.55	19.51
November	320.78	85.40	235.38	350.66	16.47
December	316.79	76.49	240.30	360.75	7.80

Annual Sum or Average	4985.44	1837.63	3147.81	5530.02	150.28
Minimum of Months	290.55	50.45	235.38	341.99	2.88
Maximum of Months	510.47	247.10	284.44	561.43	26.72

Table of Contents
Report: WINDOW ZONE SUMMARY
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN RATE [W]	ZONE WINDOWS TOTAL HEAT LOSS RATE [W]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]
January	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: WINDOW ZONE SUMMARY
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN RATE [W]	ZONE WINDOWS TOTAL HEAT LOSS RATE [W]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]
January	859.54	13.58	669.23	154.95	514.28	0.00	0.00
February	779.47	11.31	584.35	60.91	523.44	0.00	0.00
March	771.83	6.84	578.17	37.52	540.64	0.00	0.00
April	722.61	10.61	552.75	22.08	530.67	0.00	0.00
May	621.00	18.01	471.22	5.82	465.39	0.00	0.00
June	566.97	44.55	487.52	1.39	486.14	0.00	0.00
July	568.77	54.66	496.98	1.98	495.00	0.00	0.00
August	585.31	63.62	518.55	16.52	502.03	0.00	0.00
September	712.58	87.48	647.96	84.62	563.34	0.00	0.00
October	725.20	60.94	644.24	77.39	566.85	0.00	0.00
November	709.67	54.59	619.52	99.54	519.98	0.00	0.00
December	882.49	21.83	726.39	198.03	528.36	0.00	0.00

Annual Sum or Average	708.54	37.42	583.13	63.54	519.59	0.00	0.00
Minimum of Months	566.97	6.84	471.22	1.39	465.39	0.00	0.00
Maximum of Months	882.49	87.48	726.39	198.03	566.85	0.00	0.00

Table of Contents
Report: WINDOW ZONE SUMMARY
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN RATE [W]	ZONE WINDOWS TOTAL HEAT LOSS RATE [W]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]
January	719.90	6.06	639.66	277.84	361.83	0.00	0.00
February	638.32	4.77	557.02	169.15	387.86	0.00	0.00
March	671.65	3.21	590.35	193.30	397.06	0.00	0.00
April	583.73	5.11	513.58	155.47	358.11	0.00	0.00
May	459.68	8.19	401.67	98.95	302.72	0.00	0.00
June	446.28	19.08	410.79	92.55	318.24	0.00	0.00
July	479.74	22.89	444.33	112.17	332.16	0.00	0.00
August	488.63	26.03	455.63	120.10	335.53	0.00	0.00
September	620.11	33.50	584.91	216.38	368.54	0.00	0.00
October	722.65	24.99	675.79	283.67	392.12	0.00	0.00
November	744.01	22.02	693.33	322.93	370.41	0.00	0.00
December	724.37	9.84	657.33	282.80	374.53	0.00	0.00

Annual Sum or Average	608.11	15.51	552.01	193.94	358.06	0.00	0.00
Minimum of Months	446.28	3.21	401.67	92.55	302.72	0.00	0.00
Maximum of Months	744.01	33.50	693.33	322.93	397.06	0.00	0.00

Table of Contents
Report: WINDOW ZONE SUMMARY
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN RATE [W]	ZONE WINDOWS TOTAL HEAT LOSS RATE [W]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]
January	837.00	15.81	675.66	11.16	664.51	0.00	0.00
February	947.83	12.38	765.91	28.21	737.70	0.00	0.00
March	1187.50	8.33	987.33	172.24	815.09	0.00	0.00
April	1395.33	13.32	1193.93	364.99	828.94	0.00	0.00
May	1467.55	21.75	1273.22	521.53	751.68	0.00	0.00
June	1661.56	50.55	1512.61	670.07	842.54	0.00	0.00
July	1663.42	60.75	1521.47	645.80	875.67	0.00	0.00
August	1333.18	69.02	1220.81	411.66	809.15	0.00	0.00
September	1163.25	88.91	1077.90	282.81	795.09	0.00	0.00
October	967.08	65.39	885.03	125.23	759.79	0.00	0.00
November	785.11	57.41	709.71	33.85	675.86	0.00	0.00
December	781.63	25.43	662.28	3.28	659.00	0.00	0.00

Annual Sum or Average	1183.71	40.86	1041.83	273.86	767.97	0.00	0.00
Minimum of Months	781.63	8.33	662.28	3.28	659.00	0.00	0.00
Maximum of Months	1663.42	88.91	1521.47	670.07	875.67	0.00	0.00

Table of Contents
Report: WINDOW ZONE SUMMARY
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN RATE [W]	ZONE WINDOWS TOTAL HEAT LOSS RATE [W]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]
January	503.70	6.49	430.30	109.35	320.95	0.00	0.00
February	508.91	5.12	432.36	75.07	357.29	0.00	0.00
March	577.42	3.88	499.52	117.20	382.31	0.00	0.00
April	713.13	6.47	630.94	243.48	387.46	0.00	0.00
May	754.61	10.84	674.92	332.12	342.79	0.00	0.00
June	753.41	22.21	695.15	326.23	368.91	0.00	0.00
July	703.43	25.21	650.59	280.01	370.58	0.00	0.00
August	710.12	28.42	659.11	286.02	373.09	0.00	0.00
September	757.92	37.11	708.99	323.89	385.10	0.00	0.00
October	614.99	26.22	569.52	195.06	374.47	0.00	0.00
November	487.02	22.88	445.53	118.61	326.92	0.00	0.00
December	484.88	10.49	425.80	102.81	322.99	0.00	0.00

Annual Sum or Average	631.28	17.15	569.11	209.78	359.34	0.00	0.00
Minimum of Months	484.88	3.88	425.80	75.07	320.95	0.00	0.00
Maximum of Months	757.92	37.11	708.99	332.12	387.46	0.00	0.00

Table of Contents
Report: WINDOW ZONE SUMMARY
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN RATE [W]	ZONE WINDOWS TOTAL HEAT LOSS RATE [W]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION RATE [W]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION RATE [W]
January	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: WINDOW ENERGY ZONE SUMMARY
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN ENERGY [kWh]	ZONE WINDOWS TOTAL HEAT LOSS ENERGY [kWh]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]
January	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: WINDOW ENERGY ZONE SUMMARY
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN ENERGY [kWh]	ZONE WINDOWS TOTAL HEAT LOSS ENERGY [kWh]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]
January	639.49	10.10	497.91	115.28	382.63	0.00	0.00
February	523.80	7.60	392.68	40.93	351.75	0.00	0.00
March	574.24	5.09	430.16	27.92	402.24	0.00	0.00
April	520.28	7.64	397.98	15.89	382.09	0.00	0.00
May	462.02	13.40	350.58	4.33	346.25	0.00	0.00
June	408.22	32.08	351.02	1.00	350.02	0.00	0.00
July	423.17	40.67	369.75	1.48	368.28	0.00	0.00
August	435.47	47.33	385.80	12.29	373.51	0.00	0.00
September	513.05	62.99	466.53	60.93	405.60	0.00	0.00
October	539.55	45.34	479.31	57.58	421.73	0.00	0.00
November	510.96	39.30	446.05	71.67	374.38	0.00	0.00
December	656.58	16.24	540.44	147.34	393.10	0.00	0.00

Annual Sum or Average	6206.84	327.79	5108.21	556.63	4551.58	0.00	0.00
Minimum of Months	408.22	5.09	350.58	1.00	346.25	0.00	0.00
Maximum of Months	656.58	62.99	540.44	147.34	421.73	0.00	0.00

Table of Contents
Report: WINDOW ENERGY ZONE SUMMARY
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN ENERGY [kWh]	ZONE WINDOWS TOTAL HEAT LOSS ENERGY [kWh]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]
January	535.61	4.51	475.91	206.71	269.20	0.00	0.00
February	428.95	3.21	374.31	113.67	260.64	0.00	0.00
March	499.70	2.39	439.22	143.81	295.41	0.00	0.00
April	420.29	3.68	369.78	111.94	257.84	0.00	0.00
May	342.00	6.10	298.84	73.62	225.22	0.00	0.00
June	321.32	13.73	295.77	66.64	229.13	0.00	0.00
July	356.93	17.03	330.58	83.45	247.13	0.00	0.00
August	363.54	19.37	338.99	89.35	249.64	0.00	0.00
September	446.48	24.12	421.14	155.79	265.35	0.00	0.00
October	537.65	18.59	502.79	211.05	291.74	0.00	0.00
November	535.69	15.85	499.20	232.51	266.69	0.00	0.00
December	538.93	7.32	489.05	210.40	278.65	0.00	0.00

Annual Sum or Average	5327.08	135.90	4835.59	1698.95	3136.63	0.00	0.00
Minimum of Months	321.32	2.39	295.77	66.64	225.22	0.00	0.00
Maximum of Months	538.93	24.12	502.79	232.51	295.41	0.00	0.00

Table of Contents
Report: WINDOW ENERGY ZONE SUMMARY
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN ENERGY [kWh]	ZONE WINDOWS TOTAL HEAT LOSS ENERGY [kWh]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]
January	622.72	11.77	502.69	8.30	494.39	0.00	0.00
February	636.94	8.32	514.69	18.96	495.73	0.00	0.00
March	883.50	6.19	734.57	128.15	606.42	0.00	0.00
April	1004.64	9.59	859.63	262.79	596.84	0.00	0.00
May	1091.86	16.18	947.27	388.02	559.25	0.00	0.00
June	1196.32	36.40	1089.08	482.45	606.63	0.00	0.00
July	1237.59	45.20	1131.98	480.47	651.50	0.00	0.00
August	991.89	51.35	908.29	306.28	602.01	0.00	0.00
September	837.54	64.01	776.09	203.62	572.47	0.00	0.00
October	719.51	48.65	658.46	93.17	565.29	0.00	0.00
November	565.28	41.33	510.99	24.37	486.62	0.00	0.00
December	581.54	18.92	492.74	2.44	490.29	0.00	0.00

Annual Sum or Average	10369.32	357.92	9126.47	2399.03	6727.44	0.00	0.00
Minimum of Months	565.28	6.19	492.74	2.44	486.62	0.00	0.00
Maximum of Months	1237.59	64.01	1131.98	482.45	651.50	0.00	0.00

Table of Contents
Report: WINDOW ENERGY ZONE SUMMARY
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN ENERGY [kWh]	ZONE WINDOWS TOTAL HEAT LOSS ENERGY [kWh]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]
January	374.75	4.83	320.14	81.35	238.79	0.00	0.00
February	341.99	3.44	290.55	50.45	240.10	0.00	0.00
March	429.60	2.88	371.64	87.20	284.44	0.00	0.00
April	513.45	4.66	454.28	175.31	278.97	0.00	0.00
May	561.43	8.07	502.14	247.10	255.04	0.00	0.00
June	542.46	15.99	500.51	234.89	265.62	0.00	0.00
July	523.35	18.76	484.04	208.33	275.71	0.00	0.00
August	528.33	21.14	490.38	212.80	277.58	0.00	0.00
September	545.70	26.72	510.47	233.20	277.27	0.00	0.00
October	457.55	19.51	423.73	145.12	278.61	0.00	0.00
November	350.66	16.47	320.78	85.40	235.38	0.00	0.00
December	360.75	7.80	316.79	76.49	240.30	0.00	0.00

Annual Sum or Average	5530.02	150.28	4985.44	1837.63	3147.81	0.00	0.00
Minimum of Months	341.99	2.88	290.55	50.45	235.38	0.00	0.00
Maximum of Months	561.43	26.72	510.47	247.10	284.44	0.00	0.00

Table of Contents
Report: WINDOW ENERGY ZONE SUMMARY
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE WINDOWS TOTAL HEAT GAIN ENERGY [kWh]	ZONE WINDOWS TOTAL HEAT LOSS ENERGY [kWh]	ZONE WINDOWS TOTAL TRANSMITTED SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]	ZONE EXTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED DIFFUSE SOLAR RADIATION ENERGY [kWh]	ZONE INTERIOR WINDOWS TOTAL TRANSMITTED BEAM SOLAR RADIATION ENERGY [kWh]
January	0.00	0.00	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Minimum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: AVERAGE OUTDOOR CONDITIONS
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE OUTDOOR AIR DRYBULB TEMPERATURE [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE [C]	SITE OUTDOOR AIR DEWPOINT TEMPERATURE [C]	SITE WIND SPEED [m/s]	SITE SKY TEMPERATURE [C]	SITE DIFFUSE SOLAR RADIATION RATE PER AREA [W/m2]	SITE DIRECT SOLAR RADIATION RATE PER AREA [W/m2]	RAINING []
January	24.18	20.07	18.16	1.30	14.74	90.57	148.81	0.00
February	24.22	20.80	19.30	0.78	16.54	111.25	95.66	0.00
March	24.46	21.07	19.61	0.79	16.25	114.63	110.96	0.00
April	24.15	20.60	19.02	1.01	14.79	102.53	148.50	0.00
May	23.96	20.00	18.16	1.49	14.00	81.86	159.53	0.00
June	22.47	18.89	17.15	2.00	12.29	88.21	162.55	0.00
July	22.26	18.58	16.75	2.29	12.10	93.07	153.13	0.00
August	22.09	18.36	16.47	2.40	11.84	95.32	149.33	0.00
September	21.59	17.98	16.15	2.50	10.76	93.93	194.69	0.00
October	22.10	18.41	16.55	2.49	11.43	100.91	170.28	0.00
November	22.26	18.49	16.55	2.40	12.01	90.97	159.14	0.00
December	23.60	19.15	16.98	2.10	12.87	92.21	144.40	0.00

Annual Sum or Average	23.11	19.36	17.56	1.80	13.28	96.19	150.01
Minimum of Months	21.59	17.98	16.15	0.78	10.76	81.86	95.66	0.00
Maximum of Months	24.46	21.07	19.61	2.50	16.54	114.63	194.69	0.00

Table of Contents
Report: OUTDOOR CONDITIONS MAXIMUM DRYBULB
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE OUTDOOR AIR DRYBULB TEMPERATURE {Maximum}[C]	SITE OUTDOOR AIR DRYBULB TEMPERATURE {TIMESTAMP}	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR DEWPOINT TEMPERATURE {AT MAX/MIN} [C]	SITE WIND SPEED {AT MAX/MIN} [m/s]	SITE SKY TEMPERATURE {AT MAX/MIN} [C]	SITE DIFFUSE SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]	SITE DIRECT SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]
January	31.30	19-JAN-14:00	19.58	13.60	3.00	7.35	87.50	955.00
February	31.00	27-FEB-14:00	23.28	20.30	1.20	14.65	337.50	372.00
March	31.60	17-MAR-14:00	21.76	17.40	1.80	11.46	224.00	649.50
April	30.80	08-APR-14:00	20.93	16.40	2.40	9.91	133.50	807.00
May	31.70	20-MAY-14:00	20.33	14.70	1.00	8.15	69.50	926.00
June	29.40	25-JUN-14:00	19.63	14.80	2.10	7.75	80.00	868.00
July	29.50	21-JUL-12:00	18.87	13.50	1.10	10.11	428.50	173.50
August	29.60	19-AUG-14:00	19.78	15.20	4.10	8.74	166.50	701.50
September	29.10	05-SEP-14:00	20.75	16.90	2.20	9.13	80.00	924.50
October	29.90	10-OCT-14:00	20.42	15.80	6.40	8.94	101.50	859.50
November	29.70	11-NOV-14:00	21.43	17.80	8.80	12.03	208.00	573.50
December	31.40	18-DEC-14:00	19.88	14.10	2.60	8.35	134.00	793.50

Annual Sum or Average
Minimum of Months	29.10		18.87	13.50	1.00	7.35	69.50	173.50
Maximum of Months	31.70		23.28	20.30	8.80	14.65	428.50	955.00

Table of Contents
Report: OUTDOOR CONDITIONS MINIMUM DRYBULB
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE OUTDOOR AIR DRYBULB TEMPERATURE {MINIMUM}[C]	SITE OUTDOOR AIR DRYBULB TEMPERATURE {TIMESTAMP}	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR DEWPOINT TEMPERATURE {AT MAX/MIN} [C]	SITE WIND SPEED {AT MAX/MIN} [m/s]	SITE SKY TEMPERATURE {AT MAX/MIN} [C]	SITE DIFFUSE SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]	SITE DIRECT SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]
January	17.60	24-JAN-05:00	15.84	15.00	0.30	12.03	0.00	0.00
February	17.70	09-FEB-05:00	16.16	15.30	0.00	12.60	0.00	0.00
March	18.30	09-MAR-05:00	17.86	17.70	0.20	14.47	0.00	0.00
April	18.20	30-APR-05:00	15.35	13.60	0.30	10.11	0.00	0.00
May	17.80	10-MAY-05:00	17.26	17.00	0.10	12.41	0.00	0.00
June	16.20	09-JUN-05:00	16.20	16.20	1.90	11.27	0.00	0.00
July	15.90	16-JUL-05:00	13.22	11.40	1.70	8.54	0.00	0.00
August	15.10	05-AUG-05:00	13.25	12.00	0.50	7.95	0.00	0.00
September	14.90	12-SEP-05:00	12.84	11.60	3.50	7.15	0.00	0.00
October	15.30	02-OCT-05:00	14.59	14.20	1.10	6.15	0.00	0.00
November	15.10	15-NOV-05:00	13.25	12.00	0.20	3.27	17.00	293.00
December	17.00	28-DEC-05:00	15.04	13.90	3.10	10.11	0.00	0.00

Annual Sum or Average
Minimum of Months	14.90		12.84	11.40	0.00	3.27	0.00	0.00
Maximum of Months	18.30		17.86	17.70	3.50	14.47	17.00	293.00

Table of Contents
Report: OUTDOOR CONDITIONS MAXIMUM WETBULB
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE OUTDOOR AIR WETBULB TEMPERATURE {Maximum}[C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR DEWPOINT TEMPERATURE {AT MAX/MIN} [C]	SITE WIND SPEED {AT MAX/MIN} [m/s]	SITE SKY TEMPERATURE {AT MAX/MIN} [C]	SITE DIFFUSE SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]	SITE DIRECT SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]
January	24.06	27-JAN-13:00	27.80	22.70	3.70	18.82	336.00	34.00
February	25.53	22-FEB-15:00	30.10	24.10	1.70	19.87	281.50	76.00
March	25.17	22-MAR-14:00	28.50	24.10	2.20	21.96	169.00	3.00
April	24.63	07-APR-14:00	29.30	23.10	1.60	19.52	204.00	34.00
May	24.42	06-MAY-13:00	27.70	23.20	2.10	19.35	274.00	14.00
June	23.34	19-JUN-14:00	27.70	21.80	0.50	16.12	290.50	289.50
July	22.74	31-JUL-13:00	26.70	21.20	5.20	16.49	343.50	47.00
August	22.57	28-AUG-16:00	25.10	21.60	0.60	17.75	112.50	42.00
September	22.61	24-SEP-15:00	25.60	21.50	4.20	18.46	180.00	57.00
October	22.28	19-OCT-13:00	25.40	21.10	6.00	16.30	393.00	189.00
November	23.04	19-NOV-15:00	27.20	21.50	5.80	17.57	185.00	23.00
December	23.47	16-DEC-15:00	28.20	21.60	2.60	17.75	176.50	337.00

Annual Sum or Average
Minimum of Months	22.28		25.10	21.10	0.50	16.12	112.50	3.00
Maximum of Months	25.53		30.10	24.10	6.00	21.96	393.00	337.00

Table of Contents
Report: OUTDOOR CONDITIONS MAXIMUM DEW POINT
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE OUTDOOR AIR DEWPOINT TEMPERATURE {Maximum}[C]	SITE OUTDOOR AIR DEWPOINT TEMPERATURE {TIMESTAMP}	SITE OUTDOOR AIR DRYBULB TEMPERATURE {AT MAX/MIN} [C]	SITE OUTDOOR AIR WETBULB TEMPERATURE {AT MAX/MIN} [C]	SITE WIND SPEED {AT MAX/MIN} [m/s]	SITE SKY TEMPERATURE {AT MAX/MIN} [C]	SITE DIFFUSE SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]	SITE DIRECT SOLAR RADIATION RATE PER AREA {AT MAX/MIN} [W/m2]
January	22.70	01-JAN-18:00	26.90	23.83	0.70	21.09	0.00	0.00
February	24.10	22-FEB-15:00	30.10	25.53	1.70	19.87	281.50	76.00
March	24.10	14-MAR-19:00	24.70	24.19	0.20	22.81	0.00	0.00
April	23.20	05-APR-07:00	24.20	23.57	0.40	19.35	172.50	11.50
May	23.20	06-MAY-13:00	27.70	24.42	2.10	19.35	274.00	14.00
June	21.80	03-JUN-14:00	25.20	22.66	0.90	18.64	232.00	148.50
July	21.50	03-JUL-10:00	24.70	22.46	0.70	17.57	314.50	16.00
August	21.60	17-AUG-08:00	22.50	21.89	1.90	18.99	115.50	0.00
September	21.50	24-SEP-14:00	25.90	22.60	3.50	16.30	285.50	58.50
October	21.10	12-OCT-08:00	22.80	21.56	1.80	17.75	210.50	1.50
November	21.50	16-NOV-12:00	23.20	21.95	1.50	19.52	122.00	0.00
December	21.60	01-DEC-13:00	27.60	23.25	0.70	20.22	269.00	47.00

Annual Sum or Average
Minimum of Months	21.10		22.50	21.56	0.20	16.30	0.00	0.00
Maximum of Months	24.10		30.10	25.53	3.50	22.81	314.50	148.50

Table of Contents
Report: OUTDOOR GROUND CONDITIONS
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE GROUND TEMPERATURE [C]	SITE SURFACE GROUND TEMPERATURE [C]	SITE DEEP GROUND TEMPERATURE [C]	SITE MAINS WATER TEMPERATURE [C]	SITE GROUND REFLECTED SOLAR RADIATION RATE PER AREA [W/m2]	SNOW ON GROUND []
January	20.03	13.00	16.00	10.00	38.48	0.00
February	20.03	13.00	16.00	10.00	36.21	0.00
March	20.13	13.00	16.00	10.00	38.82	0.00
April	20.30	13.00	16.00	10.00	41.57	0.00
May	20.43	13.00	16.00	10.00	38.06	0.00
June	20.52	13.00	16.00	10.00	39.02	0.00
July	20.62	13.00	16.00	10.00	38.76	0.00
August	20.77	13.00	16.00	10.00	39.64	0.00
September	20.78	13.00	16.00	10.00	46.44	0.00
October	20.55	13.00	16.00	10.00	44.11	0.00
November	20.44	13.00	16.00	10.00	40.09	0.00
December	20.20	13.00	16.00	10.00	37.57	0.00

Annual Sum or Average	20.40	13.00	16.00	10.00	39.91
Minimum of Months	20.03	13.00	16.00	10.00	36.21	0.00
Maximum of Months	20.78	13.00	16.00	10.00	46.44	0.00

Table of Contents
Report: GENERATOR REPORT
For: SMALLMICROTURBINE
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	GENERATOR PRODUCED ELECTRIC ENERGY [kWh]	GENERATOR DIESEL ENERGY []	GENERATOR GAS ENERGY []	GENERATOR PRODUCED ELECTRIC ENERGY {HOURS NON-ZERO} [HOURS]	GENERATOR TOTAL HEAT RECOVERY []	GENERATOR JACKET HEAT RECOVERY ENERGY []	GENERATOR LUBE HEAT RECOVERY ENERGY []	GENERATOR EXHAUST HEAT RECOVERY ENERGY []	GENERATOR EXHAUST AIR TEMPERATURE []
January	1006.55	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00
February	908.75	0.00	0.00	672.00	0.00	0.00	0.00	0.00	0.00
March	1003.67	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00
April	974.46	0.00	0.00	720.00	0.00	0.00	0.00	0.00	0.00
May	1008.93	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00
June	991.56	0.00	0.00	720.00	0.00	0.00	0.00	0.00	0.00
July	1026.85	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00
August	1028.59	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00
September	1000.58	0.00	0.00	720.00	0.00	0.00	0.00	0.00	0.00
October	1028.57	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00
November	993.72	0.00	0.00	720.00	0.00	0.00	0.00	0.00	0.00
December	1012.72	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	11984.96			8760.00
Minimum of Months	908.75	0.00	0.00	672.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	1028.59	0.00	0.00	744.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: DAYLIGHTING REPORT
For: Environment
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	SITE EXTERIOR BEAM NORMAL ILLUMINANCE {HOURS NON-ZERO} [HOURS]	DAYLIGHTING LIGHTING POWER MULTIPLIER []	DAYLIGHTING LIGHTING POWER MULTIPLIER []	DAYLIGHTING REFERENCE POINT 1 ILLUMINANCE []	DAYLIGHTING REFERENCE POINT 1 GLARE INDEX []	DAYLIGHTING REFERENCE POINT 2 ILLUMINANCE []	DAYLIGHTING REFERENCE POINT 2 GLARE INDEX []
January	307.00	0.00	0.00	0.00	0.00	0.00	0.00
February	275.25	0.00	0.00	0.00	0.00	0.00	0.00
March	321.50	0.00	0.00	0.00	0.00	0.00	0.00
April	305.50	0.00	0.00	0.00	0.00	0.00	0.00
May	294.50	0.00	0.00	0.00	0.00	0.00	0.00
June	312.00	0.00	0.00	0.00	0.00	0.00	0.00
July	319.75	0.00	0.00	0.00	0.00	0.00	0.00
August	324.00	0.00	0.00	0.00	0.00	0.00	0.00
September	316.25	0.00	0.00	0.00	0.00	0.00	0.00
October	320.00	0.00	0.00	0.00	0.00	0.00	0.00
November	292.00	0.00	0.00	0.00	0.00	0.00	0.00
December	304.00	0.00	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	3691.75
Minimum of Months	275.25	0.00	0.00	0.00	0.00	0.00	0.00
Maximum of Months	324.00	0.00	0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: SPACE1-1 ZONE COIL
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY [kWh]	HEATING COIL HEATING RATE {Maximum}[W]	HEATING COIL HEATING RATE {TIMESTAMP}	COOLING COIL TOTAL COOLING ENERGY []	COOLING COIL SENSIBLE COOLING ENERGY []	COOLING COIL TOTAL COOLING RATE []	COOLING COIL SENSIBLE COOLING RATE []	COOLING COIL WETTED AREA FRACTION []
January	70.96	6879.79	24-JAN-06:02	0.00	0.00	0.00	0.00	0.00
February	61.88	6862.66	15-FEB-06:02	0.00	0.00	0.00	0.00	0.00
March	59.89	6735.72	05-MAR-06:03	0.00	0.00	0.00	0.00	0.00
April	86.22	7192.36	02-APR-06:03	0.00	0.00	0.00	0.00	0.00
May	89.94	7159.51	10-MAY-06:03	0.00	0.00	0.00	0.00	0.00
June	84.87	7214.90	17-JUN-06:03	0.00	0.00	0.00	0.00	0.00
July	96.84	7200.67	05-JUL-06:03	0.00	0.00	0.00	0.00	0.00
August	91.27	7249.76	02-AUG-06:03	0.00	0.00	0.00	0.00	0.00
September	86.57	7244.90	09-SEP-06:03	0.00	0.00	0.00	0.00	0.00
October	69.20	6920.59	31-OCT-06:03	0.00	0.00	0.00	0.00	0.00
November	65.27	6897.67	13-NOV-06:03	0.00	0.00	0.00	0.00	0.00
December	67.01	6899.66	26-DEC-06:03	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	929.92
Minimum of Months	59.89	6735.72		0.00	0.00	0.00	0.00	0.00
Maximum of Months	96.84	7249.76		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: SPACE2-1 ZONE COIL
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY [kWh]	HEATING COIL HEATING RATE {Maximum}[W]	HEATING COIL HEATING RATE {TIMESTAMP}	COOLING COIL TOTAL COOLING ENERGY []	COOLING COIL SENSIBLE COOLING ENERGY []	COOLING COIL TOTAL COOLING RATE []	COOLING COIL SENSIBLE COOLING RATE []	COOLING COIL WETTED AREA FRACTION []
January	30.12	3754.90	24-JAN-06:02	0.00	0.00	0.00	0.00	0.00
February	26.60	3745.14	15-FEB-06:02	0.00	0.00	0.00	0.00	0.00
March	25.68	3673.74	05-MAR-06:03	0.00	0.00	0.00	0.00	0.00
April	40.79	3929.97	02-APR-06:03	0.00	0.00	0.00	0.00	0.00
May	45.88	3911.46	10-MAY-06:03	0.00	0.00	0.00	0.00	0.00
June	40.17	3942.70	17-JUN-06:03	0.00	0.00	0.00	0.00	0.00
July	45.82	3933.43	16-JUL-06:03	0.00	0.00	0.00	0.00	0.00
August	42.86	3914.00	08-AUG-06:03	0.00	0.00	0.00	0.00	0.00
September	37.81	3940.11	11-SEP-06:03	0.00	0.00	0.00	0.00	0.00
October	17.06	3753.93	04-OCT-06:02	0.00	0.00	0.00	0.00	0.00
November	16.77	3764.83	13-NOV-06:03	0.00	0.00	0.00	0.00	0.00
December	26.70	3765.91	26-DEC-06:03	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	396.25
Minimum of Months	16.77	3673.74		0.00	0.00	0.00	0.00	0.00
Maximum of Months	45.88	3942.70		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: SPACE3-1 ZONE COIL
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY [kWh]	HEATING COIL HEATING RATE {Maximum}[W]	HEATING COIL HEATING RATE {TIMESTAMP}	COOLING COIL TOTAL COOLING ENERGY []	COOLING COIL SENSIBLE COOLING ENERGY []	COOLING COIL TOTAL COOLING RATE []	COOLING COIL SENSIBLE COOLING RATE []	COOLING COIL WETTED AREA FRACTION []
January	128.52	6117.32	24-JAN-06:02	0.00	0.00	0.00	0.00	0.00
February	108.54	6102.08	15-FEB-06:02	0.00	0.00	0.00	0.00	0.00
March	103.32	5989.68	05-MAR-06:03	0.00	0.00	0.00	0.00	0.00
April	176.06	6389.96	02-APR-06:03	0.00	0.00	0.00	0.00	0.00
May	196.16	6360.92	10-MAY-06:03	0.00	0.00	0.00	0.00	0.00
June	154.29	6453.97	13-JUN-06:03	0.00	0.00	0.00	0.00	0.00
July	181.44	6461.03	12-JUL-06:03	0.00	0.00	0.00	0.00	0.00
August	177.59	6440.72	02-AUG-06:03	0.00	0.00	0.00	0.00	0.00
September	173.98	6436.43	09-SEP-06:03	0.00	0.00	0.00	0.00	0.00
October	106.42	6153.44	31-OCT-06:03	0.00	0.00	0.00	0.00	0.00
November	110.23	6133.05	13-NOV-06:03	0.00	0.00	0.00	0.00	0.00
December	123.69	6134.78	26-DEC-06:03	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	1740.25
Minimum of Months	103.32	5989.68		0.00	0.00	0.00	0.00	0.00
Maximum of Months	196.16	6461.03		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: SPACE4-1 ZONE COIL
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY [kWh]	HEATING COIL HEATING RATE {Maximum}[W]	HEATING COIL HEATING RATE {TIMESTAMP}	COOLING COIL TOTAL COOLING ENERGY []	COOLING COIL SENSIBLE COOLING ENERGY []	COOLING COIL TOTAL COOLING RATE []	COOLING COIL SENSIBLE COOLING RATE []	COOLING COIL WETTED AREA FRACTION []
January	82.56	3060.00	24-JAN-06:02	0.00	0.00	0.00	0.00	0.00
February	71.00	3052.19	15-FEB-06:02	0.00	0.00	0.00	0.00	0.00
March	71.48	2995.21	05-MAR-06:03	0.00	0.00	0.00	0.00	0.00
April	131.41	3196.54	02-APR-06:03	0.00	0.00	0.00	0.00	0.00
May	151.04	3181.83	10-MAY-06:03	0.00	0.00	0.00	0.00	0.00
June	117.54	3229.04	13-JUN-06:03	0.00	0.00	0.00	0.00	0.00
July	143.93	3232.61	12-JUL-06:03	0.00	0.00	0.00	0.00	0.00
August	129.83	3222.29	02-AUG-06:03	0.00	0.00	0.00	0.00	0.00
September	127.06	3220.12	09-SEP-06:03	0.00	0.00	0.00	0.00	0.00
October	77.75	3078.30	31-OCT-06:03	0.00	0.00	0.00	0.00	0.00
November	75.60	3067.88	13-NOV-06:03	0.00	0.00	0.00	0.00	0.00
December	77.68	3068.73	26-DEC-06:03	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	1256.89
Minimum of Months	71.00	2995.21		0.00	0.00	0.00	0.00	0.00
Maximum of Months	151.04	3232.61		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: SPACE5-1 ZONE COIL
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY [kWh]	HEATING COIL HEATING RATE {Maximum}[W]	HEATING COIL HEATING RATE {TIMESTAMP}	COOLING COIL TOTAL COOLING ENERGY []	COOLING COIL SENSIBLE COOLING ENERGY []	COOLING COIL TOTAL COOLING RATE []	COOLING COIL SENSIBLE COOLING RATE []	COOLING COIL WETTED AREA FRACTION []
January	100.13	7278.50	24-JAN-06:02	0.00	0.00	0.00	0.00	0.00
February	86.96	7259.38	15-FEB-06:02	0.00	0.00	0.00	0.00	0.00
March	86.59	7152.31	25-MAR-06:04	0.00	0.00	0.00	0.00	0.00
April	113.09	7715.56	11-APR-06:04	0.00	0.00	0.00	0.00	0.00
May	115.30	7686.84	29-MAY-06:04	0.00	0.00	0.00	0.00	0.00
June	101.16	7700.09	13-JUN-06:03	0.00	0.00	0.00	0.00	0.00
July	113.74	7708.88	12-JUL-06:03	0.00	0.00	0.00	0.00	0.00
August	104.29	7744.09	27-AUG-06:04	0.00	0.00	0.00	0.00	0.00
September	99.64	7678.22	09-SEP-06:03	0.00	0.00	0.00	0.00	0.00
October	88.26	7323.31	31-OCT-06:03	0.00	0.00	0.00	0.00	0.00
November	85.44	7297.84	13-NOV-06:03	0.00	0.00	0.00	0.00	0.00
December	91.93	7299.92	26-DEC-06:03	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	1186.53
Minimum of Months	85.44	7152.31		0.00	0.00	0.00	0.00	0.00
Maximum of Months	115.30	7744.09		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: MAIN HEATING COIL 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY [kWh]	HEATING COIL HEATING RATE {Maximum}[W]	HEATING COIL HEATING RATE {TIMESTAMP}	COOLING COIL TOTAL COOLING ENERGY []	COOLING COIL SENSIBLE COOLING ENERGY []	COOLING COIL TOTAL COOLING RATE []	COOLING COIL SENSIBLE COOLING RATE []	COOLING COIL WETTED AREA FRACTION []
January	0.00	0.00	01-JAN-00:15	0.00	0.00	0.00	0.00	0.00
February	0.00	0.00	01-FEB-00:15	0.00	0.00	0.00	0.00	0.00
March	0.00	0.00	01-MAR-00:15	0.00	0.00	0.00	0.00	0.00
April	0.00	0.00	01-APR-00:15	0.00	0.00	0.00	0.00	0.00
May	0.00	0.00	01-MAY-00:15	0.00	0.00	0.00	0.00	0.00
June	0.00	0.00	01-JUN-00:15	0.00	0.00	0.00	0.00	0.00
July	0.00	0.00	01-JUL-00:15	0.00	0.00	0.00	0.00	0.00
August	0.00	0.00	01-AUG-00:15	0.00	0.00	0.00	0.00	0.00
September	0.00	0.00	01-SEP-00:15	0.00	0.00	0.00	0.00	0.00
October	0.00	0.00	01-OCT-00:15	0.00	0.00	0.00	0.00	0.00
November	0.00	0.00	01-NOV-00:15	0.00	0.00	0.00	0.00	0.00
December	0.00	0.00	01-DEC-00:15	0.00	0.00	0.00	0.00	0.00

Annual Sum or Average	0.00
Minimum of Months	0.00	0.00		0.00	0.00	0.00	0.00	0.00
Maximum of Months	0.00	0.00		0.00	0.00	0.00	0.00	0.00

Table of Contents
Report: COIL REPORT
For: MAIN COOLING COIL 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	HEATING COIL HEATING ENERGY []	HEATING COIL HEATING RATE []	COOLING COIL TOTAL COOLING ENERGY [kWh]	COOLING COIL SENSIBLE COOLING ENERGY [kWh]	COOLING COIL TOTAL COOLING RATE {Maximum}[W]	COOLING COIL TOTAL COOLING RATE {TIMESTAMP}	COOLING COIL SENSIBLE COOLING RATE {AT MAX/MIN} [W]	COOLING COIL WETTED AREA FRACTION []
January	0.00	0.00	4307.95	2921.71	23070.66	22-JAN-15:00	12185.17	0.43
February	0.00	0.00	3946.41	2597.40	28735.41	22-FEB-16:00	15500.24	0.42
March	0.00	0.00	4628.45	2750.38	27678.94	22-MAR-11:00	16081.92	0.40
April	0.00	0.00	5356.64	3290.20	27696.08	11-APR-15:00	13214.61	0.43
May	0.00	0.00	5418.21	3356.82	27172.92	06-MAY-14:00	12937.79	0.43
June	0.00	0.00	4195.00	2808.46	25671.16	19-JUN-15:00	13665.36	0.39
July	0.00	0.00	4768.30	3144.03	23893.63	29-JUL-15:00	15132.55	0.43
August	0.00	0.00	4327.69	2979.02	22883.78	28-AUG-16:00	11108.87	0.41
September	0.00	0.00	4098.53	2845.59	23779.00	24-SEP-15:00	12379.00	0.41
October	0.00	0.00	3465.64	2789.08	20237.56	11-OCT-15:00	17200.49	0.43
November	0.00	0.00	3245.14	2521.45	20947.92	19-NOV-16:00	11868.84	0.41
December	0.00	0.00	3574.35	2774.40	22108.80	16-DEC-16:00	12623.20	0.41

Annual Sum or Average			51332.32	34778.54				0.42
Minimum of Months	0.00	0.00	3245.14	2521.45	20237.56		11108.87	0.39
Maximum of Months	0.00	0.00	5418.21	3356.82	28735.41		17200.49	0.43

Table of Contents
Report: PLANT LOOP DEMAND REPORT
For: HOT WATER LOOP
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PLANT SUPPLY SIDE COOLING DEMAND RATE [W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {TIMESTAMP}	PLANT SUPPLY SIDE HEATING DEMAND RATE [W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {TIMESTAMP}
January	0.00	0.00	01-JAN-00:15	564.81	58847.74	10-JAN-06:02
February	0.00	0.00	01-FEB-00:15	539.42	58768.73	15-FEB-06:02
March	0.00	0.00	01-MAR-00:15	477.56	57896.09	08-MAR-06:03
April	0.00	0.00	01-APR-00:15	764.89	58330.09	24-APR-06:03
May	0.00	0.00	01-MAY-00:15	806.50	56977.30	10-MAY-06:03
June	0.00	0.00	01-JUN-00:15	696.02	58361.77	26-JUN-06:03
July	0.00	0.00	01-JUL-00:15	786.76	56970.17	17-JUL-06:03
August	0.00	0.00	01-AUG-00:15	735.89	57650.67	05-AUG-06:03
September	0.00	0.00	01-SEP-00:15	732.83	57460.65	19-SEP-06:03
October	0.00	0.00	01-OCT-00:15	493.82	59203.26	02-OCT-06:02
November	0.00	0.00	01-NOV-00:15	499.33	58395.31	04-NOV-06:02
December	0.00	0.00	01-DEC-00:15	530.90	58760.34	11-DEC-06:02

Annual Sum or Average	0.00			636.11
Minimum of Months	0.00	0.00		477.56	56970.17
Maximum of Months	0.00	0.00		806.50	59203.26

Table of Contents
Report: PLANT LOOP DEMAND REPORT
For: CHILLED WATER LOOP
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PLANT SUPPLY SIDE COOLING DEMAND RATE [W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {TIMESTAMP}	PLANT SUPPLY SIDE HEATING DEMAND RATE [W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {TIMESTAMP}
January	5828.90	23118.52	22-JAN-15:00	0.00	0.00	01-JAN-00:15
February	5909.91	28840.25	22-FEB-16:00	0.00	0.00	01-FEB-00:15
March	6257.46	27721.28	22-MAR-11:00	0.00	0.00	01-MAR-00:15
April	7527.13	28868.59	11-APR-16:00	0.00	0.00	01-APR-00:15
May	7363.14	27603.13	06-MAY-14:00	0.00	0.00	01-MAY-00:15
June	5894.86	25880.79	19-JUN-15:00	0.00	0.00	01-JUN-00:15
July	6485.15	24104.30	31-JUL-14:30	0.00	0.00	01-JUL-00:15
August	5888.00	23086.13	28-AUG-16:00	0.00	0.00	01-AUG-00:15
September	5762.44	23971.32	24-SEP-15:00	0.00	0.00	01-SEP-00:15
October	4692.21	20273.64	11-OCT-15:00	0.00	0.00	01-OCT-00:15
November	4540.80	21075.80	19-NOV-16:00	0.00	0.00	01-NOV-00:15
December	4838.93	22159.19	16-DEC-16:00	0.00	0.00	01-DEC-00:15

Annual Sum or Average	5915.62			0.00
Minimum of Months	4540.80	20273.64		0.00	0.00
Maximum of Months	7527.13	28868.59		0.00	0.00

Table of Contents
Report: FAN REPORT
For: SUPPLY FAN 1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	FAN ELECTRIC ENERGY [kWh]	FAN RISE IN AIR TEMPERATURE [deltaC]	FAN ELECTRIC POWER {Maximum}[W]	FAN ELECTRIC POWER {TIMESTAMP}	FAN RISE IN AIR TEMPERATURE {AT MAX/MIN} [deltaC]
January	205.50	0.32	808.58	31-JAN-15:00	0.63
February	180.40	0.30	831.06	27-FEB-15:00	0.63
March	190.13	0.29	853.80	22-MAR-11:00	0.63
April	187.86	0.33	734.99	02-APR-06:03	0.64
May	195.96	0.33	734.99	10-MAY-06:03	0.64
June	171.82	0.30	734.99	04-JUN-06:03	0.64
July	196.82	0.33	751.16	12-JUL-10:30	0.64
August	188.49	0.32	749.73	01-AUG-10:30	0.64
September	180.38	0.31	734.99	11-SEP-06:03	0.64
October	211.64	0.31	826.07	11-OCT-15:00	0.63
November	190.56	0.30	820.03	13-NOV-16:00	0.63
December	198.10	0.30	800.15	12-DEC-15:00	0.63

Annual Sum or Average	2297.66	0.31
Minimum of Months	171.82	0.29	734.99		0.63
Maximum of Months	211.64	0.33	853.80		0.64

Table of Contents
Report: PUMP REPORT
For: HW CIRC PUMP
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PUMP ELECTRIC ENERGY [kWh]	PUMP FLUID HEAT GAIN ENERGY [kWh]	PUMP ELECTRIC POWER {Maximum}[W]	PUMP ELECTRIC POWER {TIMESTAMP}	PUMP SHAFT POWER {AT MAX/MIN} [W]	PUMP FLUID HEAT GAIN RATE {AT MAX/MIN} [W]	PUMP OUTLET TEMPERATURE {AT MAX/MIN} [C]	PUMP MASS FLOW RATE {AT MAX/MIN} [kg/s]
January	0.87	0.78	127.65	31-JAN-06:03	114.88	114.88	55.93	0.49
February	0.75	0.68	127.64	01-FEB-06:03	114.88	114.88	55.86	0.49
March	0.72	0.65	127.63	06-MAR-06:03	114.87	114.87	55.68	0.49
April	1.10	0.99	127.66	03-APR-06:03	114.90	114.90	56.21	0.49
May	1.17	1.05	127.69	15-MAY-06:03	114.92	114.92	56.62	0.49
June	1.02	0.92	127.72	13-JUN-06:03	114.95	114.95	57.02	0.49
July	1.18	1.06	127.72	31-JUL-06:03	114.95	114.95	57.09	0.49
August	1.11	1.00	127.68	02-AUG-06:03	114.91	114.91	56.45	0.49
September	1.07	0.96	127.70	23-SEP-06:03	114.93	114.93	56.74	0.49
October	0.75	0.68	127.64	29-OCT-06:03	114.88	114.88	55.85	0.49
November	0.74	0.67	127.69	18-NOV-06:03	114.92	114.92	56.67	0.49
December	0.81	0.73	127.62	24-DEC-06:03	114.86	114.86	55.47	0.49

Annual Sum or Average	11.29	10.16
Minimum of Months	0.72	0.65	127.62		114.86	114.86	55.47	0.49
Maximum of Months	1.18	1.06	127.72		114.95	114.95	57.09	0.49

Table of Contents
Report: PUMP REPORT
For: CW CIRC PUMP
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PUMP ELECTRIC ENERGY [kWh]	PUMP FLUID HEAT GAIN ENERGY [kWh]	PUMP ELECTRIC POWER {Maximum}[W]	PUMP ELECTRIC POWER {TIMESTAMP}	PUMP SHAFT POWER {AT MAX/MIN} [W]	PUMP FLUID HEAT GAIN RATE {AT MAX/MIN} [W]	PUMP OUTLET TEMPERATURE {AT MAX/MIN} [C]	PUMP MASS FLOW RATE {AT MAX/MIN} [kg/s]
January	41.58	37.43	178.97	22-JAN-18:00	161.07	161.07	14.37	0.70
February	36.92	33.23	190.94	22-FEB-16:00	171.85	171.85	16.45	0.75
March	41.22	37.09	189.67	22-MAR-15:45	170.70	170.70	15.40	0.74
April	72.97	65.68	301.18	18-APR-17:00	271.06	271.06	12.00	1.18
May	74.83	67.35	296.77	06-MAY-13:15	267.09	267.09	12.64	1.16
June	61.18	55.06	294.60	21-JUN-16:30	265.14	265.14	12.06	1.15
July	70.16	63.15	286.06	31-JUL-16:30	257.45	257.45	11.86	1.12
August	65.29	58.76	285.72	28-AUG-17:00	257.15	257.15	11.91	1.12
September	62.09	55.88	286.24	24-SEP-16:30	257.62	257.62	12.02	1.12
October	35.68	32.11	157.57	17-OCT-17:00	141.82	141.82	13.87	0.62
November	33.73	30.36	170.36	19-NOV-18:00	153.33	153.33	13.86	0.67
December	36.36	32.73	169.46	16-DEC-16:00	152.51	152.51	15.21	0.66

Annual Sum or Average	632.02	568.82
Minimum of Months	33.73	30.36	157.57		141.82	141.82	11.86	0.62
Maximum of Months	74.83	67.35	301.18		271.06	271.06	16.45	1.18

Table of Contents
Report: COND LOOP DEMAND REPORT
For: HOT WATER LOOP
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PLANT SUPPLY SIDE COOLING DEMAND RATE [W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {TIMESTAMP}	PLANT SUPPLY SIDE INLET TEMPERATURE {AT MAX/MIN} [C]	PLANT SUPPLY SIDE OUTLET TEMPERATURE {AT MAX/MIN} [C]	PLANT SUPPLY SIDE HEATING DEMAND RATE [W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {TIMESTAMP}
January	0.00	0.00	01-JAN-00:15	43.39	43.39	564.81	58847.74	10-JAN-06:02
February	0.00	0.00	01-FEB-00:15	44.99	44.99	539.42	58768.73	15-FEB-06:02
March	0.00	0.00	01-MAR-00:15	43.89	43.89	477.56	57896.09	08-MAR-06:03
April	0.00	0.00	01-APR-00:15	43.40	43.40	764.89	58330.09	24-APR-06:03
May	0.00	0.00	01-MAY-00:15	43.82	43.82	806.50	56977.30	10-MAY-06:03
June	0.00	0.00	01-JUN-00:15	44.36	44.36	696.02	58361.77	26-JUN-06:03
July	0.00	0.00	01-JUL-00:15	43.70	43.70	786.76	56970.17	17-JUL-06:03
August	0.00	0.00	01-AUG-00:15	44.49	44.49	735.89	57650.67	05-AUG-06:03
September	0.00	0.00	01-SEP-00:15	42.92	42.92	732.83	57460.65	19-SEP-06:03
October	0.00	0.00	01-OCT-00:15	43.30	43.30	493.82	59203.26	02-OCT-06:02
November	0.00	0.00	01-NOV-00:15	44.18	44.18	499.33	58395.31	04-NOV-06:02
December	0.00	0.00	01-DEC-00:15	43.55	43.55	530.90	58760.34	11-DEC-06:02

Annual Sum or Average	0.00					636.11
Minimum of Months	0.00	0.00		42.92	42.92	477.56	56970.17
Maximum of Months	0.00	0.00		44.99	44.99	806.50	59203.26

Table of Contents
Report: COND LOOP DEMAND REPORT
For: CHILLED WATER LOOP
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	PLANT SUPPLY SIDE COOLING DEMAND RATE [W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE COOLING DEMAND RATE {TIMESTAMP}	PLANT SUPPLY SIDE INLET TEMPERATURE {AT MAX/MIN} [C]	PLANT SUPPLY SIDE OUTLET TEMPERATURE {AT MAX/MIN} [C]	PLANT SUPPLY SIDE HEATING DEMAND RATE [W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {Maximum}[W]	PLANT SUPPLY SIDE HEATING DEMAND RATE {TIMESTAMP}
January	5828.90	23118.52	22-JAN-15:00	15.51	7.22	0.00	0.00	01-JAN-00:15
February	5909.91	28840.25	22-FEB-16:00	16.45	7.22	0.00	0.00	01-FEB-00:15
March	6257.46	27721.28	22-MAR-11:00	17.07	7.22	0.00	0.00	01-MAR-00:15
April	7527.13	28868.59	11-APR-16:00	13.25	7.22	0.00	0.00	01-APR-00:15
May	7363.14	27603.13	06-MAY-14:00	12.94	7.22	0.00	0.00	01-MAY-00:15
June	5894.86	25880.79	19-JUN-15:00	12.73	7.22	0.00	0.00	01-JUN-00:15
July	6485.15	24104.30	31-JUL-14:30	12.53	7.22	0.00	0.00	01-JUL-00:15
August	5888.00	23086.13	28-AUG-16:00	12.23	7.22	0.00	0.00	01-AUG-00:15
September	5762.44	23971.32	24-SEP-15:00	12.50	7.22	0.00	0.00	01-SEP-00:15
October	4692.21	20273.64	11-OCT-15:00	16.07	7.22	0.00	0.00	01-OCT-00:15
November	4540.80	21075.80	19-NOV-16:00	15.08	7.22	0.00	0.00	01-NOV-00:15
December	4838.93	22159.19	16-DEC-16:00	15.21	7.22	0.00	0.00	01-DEC-00:15

Annual Sum or Average	5915.62					0.00
Minimum of Months	4540.80	20273.64		12.23	7.22	0.00	0.00
Maximum of Months	7527.13	28868.59		17.07	7.22	0.00	0.00

Table of Contents
Report: ZONE TEMPERATURE OSCILLATION REPORT
For: PLENUM-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE OSCILLATING TEMPERATURES TIME {HOURS NON-ZERO} [HOURS]	ZONE PEOPLE OCCUPANT COUNT []
January	0.00	0.00
February	0.00	0.00
March	0.00	0.00
April	0.00	0.00
May	0.00	0.00
June	0.00	0.00
July	0.00	0.00
August	0.00	0.00
September	0.00	0.00
October	0.00	0.00
November	0.00	0.00
December	0.00	0.00

Annual Sum or Average	0.00
Minimum of Months	0.00	0.00
Maximum of Months	0.00	0.00

Table of Contents
Report: ZONE TEMPERATURE OSCILLATION REPORT
For: SPACE1-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE OSCILLATING TEMPERATURES TIME {HOURS NON-ZERO} [HOURS]	ZONE PEOPLE OCCUPANT COUNT {FOR HOURS SHOWN} []
January	0.00	0.00
February	0.00	0.00
March	0.00	0.00
April	0.00	0.00
May	0.00	0.00
June	0.00	0.00
July	0.00	0.00
August	0.00	0.00
September	0.00	0.00
October	0.00	0.00
November	0.00	0.00
December	0.00	0.00

Annual Sum or Average	0.00
Minimum of Months	0.00	0.00
Maximum of Months	0.00	0.00

Table of Contents
Report: ZONE TEMPERATURE OSCILLATION REPORT
For: SPACE2-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE OSCILLATING TEMPERATURES TIME {HOURS NON-ZERO} [HOURS]	ZONE PEOPLE OCCUPANT COUNT {FOR HOURS SHOWN} []
January	0.00	0.00
February	0.00	0.00
March	0.00	0.00
April	0.00	0.00
May	0.00	0.00
June	0.00	0.00
July	0.00	0.00
August	0.00	0.00
September	0.21	0.00
October	0.00	0.00
November	0.21	3.00
December	0.00	0.00

Annual Sum or Average	0.42	1.50
Minimum of Months	0.00	0.00
Maximum of Months	0.21	3.00

Table of Contents
Report: ZONE TEMPERATURE OSCILLATION REPORT
For: SPACE3-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE OSCILLATING TEMPERATURES TIME {HOURS NON-ZERO} [HOURS]	ZONE PEOPLE OCCUPANT COUNT {FOR HOURS SHOWN} []
January	0.00	0.00
February	0.00	0.00
March	0.00	0.00
April	0.00	0.00
May	0.00	0.00
June	0.00	0.00
July	0.00	0.00
August	0.00	0.00
September	0.21	0.00
October	0.00	0.00
November	0.00	0.00
December	0.00	0.00

Annual Sum or Average	0.21	0.00
Minimum of Months	0.00	0.00
Maximum of Months	0.21	0.00

Table of Contents
Report: ZONE TEMPERATURE OSCILLATION REPORT
For: SPACE4-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE OSCILLATING TEMPERATURES TIME {HOURS NON-ZERO} [HOURS]	ZONE PEOPLE OCCUPANT COUNT {FOR HOURS SHOWN} []
January	0.00	0.00
February	0.00	0.00
March	0.00	0.00
April	0.00	0.00
May	0.00	0.00
June	0.00	0.00
July	0.00	0.00
August	0.00	0.00
September	0.08	0.00
October	0.00	0.00
November	0.00	0.00
December	0.00	0.00

Annual Sum or Average	0.08	0.00
Minimum of Months	0.00	0.00
Maximum of Months	0.08	0.00

Table of Contents
Report: ZONE TEMPERATURE OSCILLATION REPORT
For: SPACE5-1
Timestamp: 2019-06-19 07:53:09
Custom Monthly Report
	ZONE OSCILLATING TEMPERATURES TIME {HOURS NON-ZERO} [HOURS]	ZONE PEOPLE OCCUPANT COUNT {FOR HOURS SHOWN} []
January	0.00	0.00
February	0.00	0.00
March	0.00	0.00
April	0.00	0.00
May	0.00	0.00
June	0.00	0.00
July	0.00	0.00
August	0.00	0.00
September	0.00	0.00
October	0.00	0.00
November	0.00	0.00
December	0.00	0.00

Annual Sum or Average	0.00
Minimum of Months	0.00	0.00
Maximum of Months	0.00	0.00

Table of Contents
Report: Economics Results Summary Report
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Annual Cost
	Electric	Gas	Other	Total
Cost [$]	2207.45	1073.95	1671.53	4952.93
Cost per Total Building Area [$/m2]	2.38	1.16	1.80	5.34
Cost per Net Conditioned Building Area [$/m2]	2.38	1.16	1.80	5.34

Tariff Summary
	Selected	Qualified	Meter	Buy or Sell	Group	Annual Cost ($)
WATER TARIFF	Yes	Yes	WATER:FACILITY	Buy	(none)	1671.53
EXAMPLEA	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	2325.05
EXAMPLEA-GAS	Yes	Yes	GAS:FACILITY	Buy	(none)	1073.95
EXAMPLEAWITHVARIABLEMONTHLYCHARGE	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	2372.93
EXAMPLEB	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	2631.79
EXAMPLEC	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3085.66
EXAMPLED	Yes	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	2251.56
EXAMPLEDWITHRATCHET	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3572.32
EXAMPLEE	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3777.24
EXAMPLEF	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3381.68
EXAMPLEFMC	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3381.68
EXAMPLEG	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3841.07
EXAMPLEH	No	Yes	ELECTRICITYPURCHASED:FACILITY	Buy	(none)	3381.68
EXAMPLEI-SELL	Yes	Yes	ELECTRICITYSURPLUSSOLD:FACILITY	Sell	(none)	-44.1
EXAMPLEI-NETMETER	No	Yes	ELECTRICITYNET:FACILITY	Net	(none)	2912.07

Table of Contents
Report: Tariff Report
For: WATER TARIFF
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	WATER:FACILITY
Selected	Yes
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	User Defined

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	141.97	128.23	141.97	137.39	141.97	137.39	141.97	141.97	137.39	141.97	137.39	141.97	1671.53	141.97
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Basis ($)	141.97	128.23	141.97	137.39	141.97	137.39	141.97	141.97	137.39	141.97	137.39	141.97	1671.53	141.97
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	141.97	128.23	141.97	137.39	141.97	137.39	141.97	141.97	137.39	141.97	137.39	141.97	1671.53	141.97
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	141.97	128.23	141.97	137.39	141.97	137.39	141.97	141.97	137.39	141.97	137.39	141.97	1671.53	141.97

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
WATERTARIFFENERGYCHARGE ($)	141.97	128.23	141.97	137.39	141.97	137.39	141.97	141.97	137.39	141.97	137.39	141.97	1671.53	141.97	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	20.28	18.32	20.28	19.63	20.28	19.63	20.28	20.28	19.63	20.28	19.63	20.28	238.79	20.28

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	20.28	18.32	20.28	19.63	20.28	19.63	20.28	20.28	19.63	20.28	19.63	20.28	238.79	20.28
TotalDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakEnergy	20.28	18.32	20.28	19.63	20.28	19.63	20.28	20.28	19.63	20.28	19.63	20.28	238.79	20.28
PeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	20.28	18.32	20.28	19.63	20.28	19.63	20.28	20.28	19.63	20.28	19.63	20.28	238.79	20.28
PeakAndShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndMidPeakEnergy	20.28	18.32	20.28	19.63	20.28	19.63	20.28	20.28	19.63	20.28	19.63	20.28	238.79	20.28
PeakAndMidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	20.28	18.32	20.28	19.63	20.28	19.63	20.28	20.28	19.63	20.28	19.63	20.28	238.79	20.28
PeakAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
WATERTARIFFENERGYCHARGE FROM TotalEnergy
EnergyCharges SUM WATERTARIFFENERGYCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEA
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	199.29	176.30	191.65	208.57	215.17	179.19	205.09	192.95	183.64	187.44	172.30	183.33	2294.93	215.17
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	2.51	2.51	2.51	2.51	2.51	2.51	2.51	2.51	2.51	2.51	2.51	2.51	30.12	2.51
Basis ($)	201.80	178.81	194.16	211.08	217.68	181.70	207.60	195.46	186.15	189.95	174.81	185.84	2325.05	217.68
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	201.80	178.81	194.16	211.08	217.68	181.70	207.60	195.46	186.15	189.95	174.81	185.84	2325.05	217.68
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	201.80	178.81	194.16	211.08	217.68	181.70	207.60	195.46	186.15	189.95	174.81	185.84	2325.05	217.68

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
FLATENERGYCHARGE ($)	199.29	176.30	191.65	208.57	215.17	179.19	205.09	192.95	183.64	187.44	172.30	183.33	2294.93	215.17	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
FLATENERGYCHARGE FROM TotalEnergy
EnergyCharges SUM FLATENERGYCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEA-GAS
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	GAS:FACILITY
Selected	Yes
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	Therm

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	74.32	66.75	72.85	75.04	78.33	74.65	78.68	77.96	75.58	74.06	71.71	74.02	893.95	78.68
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	15.00	15.00	15.00	15.00	15.00	15.00	15.00	15.00	15.00	15.00	15.00	15.00	180.00	15.00
Basis ($)	89.32	81.75	87.85	90.04	93.33	89.65	93.68	92.96	90.58	89.06	86.71	89.02	1073.95	93.68
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	89.32	81.75	87.85	90.04	93.33	89.65	93.68	92.96	90.58	89.06	86.71	89.02	1073.95	93.68
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	89.32	81.75	87.85	90.04	93.33	89.65	93.68	92.96	90.58	89.06	86.71	89.02	1073.95	93.68

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
FLATENERGYCHARGE-GAS ($)	74.32	66.75	72.85	75.04	78.33	74.65	78.68	77.96	75.58	74.06	71.71	74.02	893.95	78.68	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	148.64	133.49	145.70	150.09	156.66	149.30	157.36	155.92	151.17	148.12	143.42	148.03	1787.89	157.36

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	148.64	133.49	145.70	150.09	156.66	149.30	157.36	155.92	151.17	148.12	143.42	148.03	1787.89	157.36
TotalDemand	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
PeakEnergy	148.64	133.49	145.70	150.09	156.66	149.30	157.36	155.92	151.17	148.12	143.42	148.03	1787.89	157.36
PeakDemand	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	148.64	133.49	145.70	150.09	156.66	149.30	157.36	155.92	151.17	148.12	143.42	148.03	1787.89	157.36
PeakAndShoulderDemand	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
PeakAndMidPeakEnergy	148.64	133.49	145.70	150.09	156.66	149.30	157.36	155.92	151.17	148.12	143.42	148.03	1787.89	157.36
PeakAndMidPeakDemand	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	148.64	133.49	145.70	150.09	156.66	149.30	157.36	155.92	151.17	148.12	143.42	148.03	1787.89	157.36
PeakAndOffPeakDemand	1.03	1.03	0.8383	0.9169	1.03	1.05	1.06	1.03	1.07	0.9408	0.9492	0.9250	11.86	1.07
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
FLATENERGYCHARGE-GAS FROM TotalEnergy
EnergyCharges SUM FLATENERGYCHARGE-GAS
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEAWITHVARIABLEMONTHLYCHARGE
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	199.29	176.30	191.65	208.57	215.17	179.19	205.09	192.95	183.64	187.44	172.30	183.33	2294.93	215.17
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	1.00	2.00	3.00	4.00	5.00	6.00	7.00	8.00	9.00	10.00	11.00	12.00	78.00	12.00
Basis ($)	200.29	178.30	194.65	212.57	220.17	185.19	212.09	200.95	192.64	197.44	183.30	195.33	2372.93	220.17
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	200.29	178.30	194.65	212.57	220.17	185.19	212.09	200.95	192.64	197.44	183.30	195.33	2372.93	220.17
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	200.29	178.30	194.65	212.57	220.17	185.19	212.09	200.95	192.64	197.44	183.30	195.33	2372.93	220.17

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
FLATENERGYCHARGE ($)	199.29	176.30	191.65	208.57	215.17	179.19	205.09	192.95	183.64	187.44	172.30	183.33	2294.93	215.17	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
VARIABLEFIXEDCHARGE	1.00	2.00	3.00	4.00	5.00	6.00	7.00	8.00	9.00	10.00	11.00	12.00	78.00	12.00
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
FLATENERGYCHARGE FROM TotalEnergy
EnergyCharges SUM FLATENERGYCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEB
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	222.11	197.70	214.00	231.96	238.97	200.76	228.27	215.38	205.50	209.53	193.45	205.16	2562.79	238.97
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	5.75	5.75	5.75	5.75	5.75	5.75	5.75	5.75	5.75	5.75	5.75	5.75	69.00	5.75
Basis ($)	227.86	203.45	219.75	237.71	244.72	206.51	234.02	221.13	211.25	215.28	199.20	210.91	2631.79	244.72
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	227.86	203.45	219.75	237.71	244.72	206.51	234.02	221.13	211.25	215.28	199.20	210.91	2631.79	244.72
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	227.86	203.45	219.75	237.71	244.72	206.51	234.02	221.13	211.25	215.28	199.20	210.91	2631.79	244.72

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
BLOCKENERGYCHARGE ($)	222.11	197.70	214.00	231.96	238.97	200.76	228.27	215.38	205.50	209.53	193.45	205.16	2562.79	238.97	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
BLOCKENERGYCHARGE FROM TotalEnergy
EnergyCharges SUM BLOCKENERGYCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEC
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	170.69	151.00	164.15	178.64	184.29	153.47	175.66	165.26	157.29	160.54	147.57	157.02	1965.59	184.29
DemandCharges ($)	90.43	97.71	101.30	99.42	96.57	94.59	92.17	92.00	92.26	87.44	87.71	88.48	1120.07	101.30
ServiceCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Basis ($)	261.12	248.71	265.45	278.06	280.86	248.06	267.83	257.26	249.55	247.98	235.28	245.50	3085.66	280.86
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	261.12	248.71	265.45	278.06	280.86	248.06	267.83	257.26	249.55	247.98	235.28	245.50	3085.66	280.86
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	261.12	248.71	265.45	278.06	280.86	248.06	267.83	257.26	249.55	247.98	235.28	245.50	3085.66	280.86

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
BLOCKENERGYCHARGE ($)	170.69	151.00	164.15	178.64	184.29	153.47	175.66	165.26	157.29	160.54	147.57	157.02	1965.59	184.29	EnergyCharges
BLOCKDEMANDCHARGE ($)	90.43	97.71	101.30	99.42	96.57	94.59	92.17	92.00	92.26	87.44	87.71	88.48	1120.07	101.30	DemandCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
BLOCKENERGYCHARGE FROM TotalEnergy
BLOCKDEMANDCHARGE FROM TotalDemand
EnergyCharges SUM BLOCKENERGYCHARGE
DemandCharges SUM BLOCKDEMANDCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLED
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	Yes
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	138.02	122.63	132.90	144.23	148.65	240.01	273.26	257.68	245.73	130.09	119.95	127.33	2080.48	273.26
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	84.00	7.00
Basis ($)	145.02	129.63	139.90	151.23	155.65	247.01	280.26	264.68	252.73	137.09	126.95	134.33	2164.48	280.26
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	145.02	129.63	139.90	151.23	155.65	247.01	280.26	264.68	252.73	137.09	126.95	134.33	2164.48	280.26
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	150.00	150.00	150.00	151.23	155.65	247.01	280.26	264.68	252.73	150.00	150.00	150.00	2251.56	280.26

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
WINTERENERGYCOST ($)	138.02	122.63	132.90	144.23	148.65	0.00	0.00	0.00	0.00	130.09	119.95	127.33	1063.80	148.65	EnergyCharges
SUMMERENERGYCOST ($)	0.00	0.00	0.00	0.00	0.00	240.01	273.26	257.68	245.73	0.00	0.00	0.00	1016.68	273.26	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
WINTERENERGYCOST FROM TotalEnergy
SUMMERENERGYCOST FROM TotalEnergy
EnergyCharges SUM WINTERENERGYCOST SUMMERENERGYCOST
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEDWITHRATCHET
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	138.02	122.63	132.90	144.23	148.65	240.01	273.26	257.68	245.73	130.09	119.95	127.33	2080.48	273.26
DemandCharges ($)	94.04	100.81	104.15	102.40	99.75	160.65	157.06	156.80	157.19	91.26	91.51	92.23	1407.84	160.65
ServiceCharges ($)	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	7.00	84.00	7.00
Basis ($)	239.06	230.44	244.05	253.62	255.39	407.67	437.32	421.48	409.92	228.35	218.47	226.56	3572.32	437.32
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	239.06	230.44	244.05	253.62	255.39	407.67	437.32	421.48	409.92	228.35	218.47	226.56	3572.32	437.32
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	239.06	230.44	244.05	253.62	255.39	407.67	437.32	421.48	409.92	228.35	218.47	226.56	3572.32	437.32

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
WINTERENERGYCOST ($)	138.02	122.63	132.90	144.23	148.65	0.00	0.00	0.00	0.00	130.09	119.95	127.33	1063.80	148.65	EnergyCharges
SUMMERENERGYCOST ($)	0.00	0.00	0.00	0.00	0.00	240.01	273.26	257.68	245.73	0.00	0.00	0.00	1016.68	273.26	EnergyCharges
WINTERDEMANDCOST ($)	94.04	100.81	104.15	102.40	99.75	0.00	0.00	0.00	0.00	91.26	91.51	92.23	776.15	104.15	DemandCharges
SUMMERDEMANDCOST ($)	0.00	0.00	0.00	0.00	0.00	160.65	157.06	156.80	157.19	0.00	0.00	0.00	631.70	160.65	DemandCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
BILLINGDEMAND1	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83

Ratchets
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
BILLINGDEMAND1	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
WINTERENERGYCOST FROM TotalEnergy
SUMMERENERGYCOST FROM TotalEnergy
BILLINGDEMAND1 FROM TotalDemand TotalDemand
SUMMERDEMANDCOST FROM BILLINGDEMAND1
EnergyCharges SUM WINTERENERGYCOST SUMMERENERGYCOST
WINTERDEMANDCOST FROM BILLINGDEMAND1
DemandCharges SUM WINTERDEMANDCOST SUMMERDEMANDCOST
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEE
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	310.66	278.94	303.22	328.58	334.64	283.50	319.06	303.99	290.55	293.91	272.60	289.60	3609.24	334.64
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	14.00	14.00	14.00	14.00	14.00	14.00	14.00	14.00	14.00	14.00	14.00	14.00	168.00	14.00
Basis ($)	324.66	292.94	317.22	342.58	348.64	297.50	333.06	317.99	304.55	307.91	286.60	303.60	3777.24	348.64
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	324.66	292.94	317.22	342.58	348.64	297.50	333.06	317.99	304.55	307.91	286.60	303.60	3777.24	348.64
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	324.66	292.94	317.22	342.58	348.64	297.50	333.06	317.99	304.55	307.91	286.60	303.60	3777.24	348.64

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
BLOCKENERGYCHARGE ($)	310.66	278.94	303.22	328.58	334.64	283.50	319.06	303.99	290.55	293.91	272.60	289.60	3609.24	334.64	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
BLOCKENERGYCHARGE FROM TotalEnergy TotalDemand
EnergyCharges SUM BLOCKENERGYCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEF
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	160.76	141.85	152.86	167.33	171.66	398.68	456.10	429.99	409.53	151.83	139.54	148.55	2928.68	456.10
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	453.00	37.75
Basis ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
SUMMERONPEAK ($)	0.00	0.00	0.00	0.00	0.00	353.65	404.38	382.07	364.14	0.00	0.00	0.00	1504.25	404.38	EnergyCharges
SUMMEROFFPEAK ($)	0.00	0.00	0.00	0.00	0.00	45.03	51.72	47.92	45.38	0.00	0.00	0.00	190.05	51.72	EnergyCharges
WINTERONPEAK ($)	103.83	91.34	97.41	107.37	109.42	0.00	0.00	0.00	0.00	98.54	90.55	96.46	794.92	109.42	EnergyCharges
WINTEROFFPEAK ($)	56.93	50.51	55.46	59.95	62.25	0.00	0.00	0.00	0.00	53.28	48.99	52.09	439.46	62.25	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
PeakEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
OffPeakEnergy	2352.40	2087.09	2291.54	2477.46	2572.12	713.36	819.33	759.20	718.99	2201.85	2024.31	2152.62	21170.27	2572.12

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
MINDEMAND	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
PeakDemand	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	2352.40	2087.09	2291.54	2477.46	2572.12	713.36	819.33	759.20	718.99	2201.85	2024.31	2152.62	21170.27	2572.12
OffPeakDemand	16.81	18.15	18.83	18.48	17.95	16.66	15.84	16.01	16.23	16.25	16.30	16.45	203.96	18.83
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	0.00	0.0128	0.00	0.00	0.00	0.9175	1.29	1.09	0.9148	0.00	0.00	0.00	4.23	1.29
OffPeakExceedsPeak	0.8529	0.00	1.36	0.5063	0.5414	0.00	0.00	0.00	0.00	0.5962	0.6283	0.4098	4.89	1.36
PeakExceedsMidPeak	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
PeakAndShoulderDemand	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
PeakAndMidPeakEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
PeakAndMidPeakDemand	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
ShoulderAndOffPeakEnergy	2352.40	2087.09	2291.54	2477.46	2572.12	713.36	819.33	759.20	718.99	2201.85	2024.31	2152.62	21170.27	2572.12
ShoulderAndOffPeakDemand	16.81	18.15	18.83	18.48	17.95	16.66	15.84	16.01	16.23	16.25	16.30	16.45	203.96	18.83
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
MINDEMAND FROM TotalDemand
SUMMERONPEAK FROM PeakEnergy
SUMMEROFFPEAK FROM OffPeakEnergy
WINTERONPEAK FROM PeakEnergy
WINTEROFFPEAK FROM OffPeakEnergy
EnergyCharges SUM SUMMERONPEAK SUMMEROFFPEAK WINTERONPEAK WINTEROFFPEAK
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEFMC
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	MANUALEXAMPLE
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	160.76	141.85	152.86	167.33	171.66	398.68	456.10	429.99	409.53	151.83	139.54	148.55	2928.68	456.10
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	453.00	37.75
Basis ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
SUMMERONPEAK ($)	0.00	0.00	0.00	0.00	0.00	353.65	404.38	382.07	364.14	0.00	0.00	0.00	1504.25	404.38	EnergyCharges
SUMMEROFFPEAK ($)	0.00	0.00	0.00	0.00	0.00	45.03	51.72	47.92	45.38	0.00	0.00	0.00	190.05	51.72	EnergyCharges
WINTERONPEAK ($)	103.83	91.34	97.41	107.37	109.42	0.00	0.00	0.00	0.00	98.54	90.55	96.46	794.92	109.42	EnergyCharges
WINTEROFFPEAK ($)	56.93	50.51	55.46	59.95	62.25	0.00	0.00	0.00	0.00	53.28	48.99	52.09	439.46	62.25	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
PeakEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
OffPeakEnergy	2352.40	2087.09	2291.54	2477.46	2572.12	713.36	819.33	759.20	718.99	2201.85	2024.31	2152.62	21170.27	2572.12

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
MINDEMAND	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
PeakDemand	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	2352.40	2087.09	2291.54	2477.46	2572.12	713.36	819.33	759.20	718.99	2201.85	2024.31	2152.62	21170.27	2572.12
OffPeakDemand	16.81	18.15	18.83	18.48	17.95	16.66	15.84	16.01	16.23	16.25	16.30	16.45	203.96	18.83
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	0.00	0.0128	0.00	0.00	0.00	0.9175	1.29	1.09	0.9148	0.00	0.00	0.00	4.23	1.29
OffPeakExceedsPeak	0.8529	0.00	1.36	0.5063	0.5414	0.00	0.00	0.00	0.00	0.5962	0.6283	0.4098	4.89	1.36
PeakExceedsMidPeak	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	4.00	1.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	0.00	0.00	0.00	0.00	1.00	1.00	1.00	8.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
PeakAndShoulderDemand	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
PeakAndMidPeakEnergy	1248.72	1098.55	1171.48	1291.31	1315.90	2524.45	2886.57	2727.34	2599.35	1185.12	1089.02	1160.03	20297.85	2886.57
PeakAndMidPeakDemand	15.96	18.16	17.47	17.97	17.41	17.58	17.13	17.10	17.15	15.66	15.67	16.04	203.30	18.16
ShoulderAndOffPeakEnergy	2352.40	2087.09	2291.54	2477.46	2572.12	713.36	819.33	759.20	718.99	2201.85	2024.31	2152.62	21170.27	2572.12
ShoulderAndOffPeakDemand	16.81	18.15	18.83	18.48	17.95	16.66	15.84	16.01	16.23	16.25	16.30	16.45	203.96	18.83
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
SUMENECHARGES	0.00	0.00	0.00	0.00	0.00	398.68	456.10	429.99	409.53	0.00	0.00	0.00	1694.29	456.10
WINENECHARGES	160.76	141.85	152.86	167.33	171.66	0.00	0.00	0.00	0.00	151.83	139.54	148.55	1234.38	171.66

Computation - User Defined
SUMENECHARGES SUM SUMMERONPEAK SUMMEROFFPEAK
WINENECHARGES SUM WINTERONPEAK WINTEROFFPEAK
EnergyCharges SUM SUMENECHARGES WINENECHARGES
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEG
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	295.00	265.59	286.20	308.47	315.96	269.47	302.54	287.54	275.45	279.72	260.22	274.89	3421.07	315.96
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	35.00	35.00	35.00	35.00	35.00	35.00	35.00	35.00	35.00	35.00	35.00	35.00	420.00	35.00
Basis ($)	330.00	300.59	321.20	343.47	350.96	304.47	337.54	322.54	310.45	314.72	295.22	309.89	3841.07	350.96
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	330.00	300.59	321.20	343.47	350.96	304.47	337.54	322.54	310.45	314.72	295.22	309.89	3841.07	350.96
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	330.00	300.59	321.20	343.47	350.96	304.47	337.54	322.54	310.45	314.72	295.22	309.89	3841.07	350.96

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
ENERGYFIRST200KWHPERKW ($)	3361.58	3185.65	3463.02	3695.87	3589.83	3237.81	3426.48	3419.93	3318.34	3250.38	3113.33	3289.17	40351.39	3695.87	none
COSTOFFIRST200KWHPERKW ($)	278.67	265.59	286.20	303.50	295.62	269.47	283.49	283.00	275.45	270.40	260.22	273.29	3344.91	303.50	EnergyCharges
COSTOFRESTOFENERGY ($)	16.34	0.00	0.00	4.97	20.34	0.00	19.06	4.54	0.00	9.32	0.00	1.60	76.16	20.34	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
ENERGYFIRST200KWHPERKW	3361.58	3185.65	3463.02	3695.87	3589.83	3237.81	3426.48	3419.93	3318.34	3250.38	3113.33	3289.17	40351.39	3695.87
RESTOFENERGY	239.54	0.00	0.00	72.90	298.19	0.00	279.42	66.61	0.00	136.59	0.00	23.47	1116.72	298.19

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
ENERGYFIRST200KWHPERKW FROM TotalEnergy TotalDemand
RESTOFENERGY FROM ENERGYFIRST200KWHPERKW
COSTOFFIRST200KWHPERKW FROM ENERGYFIRST200KWHPERKW
COSTOFRESTOFENERGY FROM RESTOFENERGY TotalDemand
EnergyCharges SUM COSTOFFIRST200KWHPERKW COSTOFRESTOFENERGY
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEH
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYPURCHASED:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	160.76	141.85	152.86	167.33	171.66	398.68	456.10	429.99	409.53	151.83	139.54	148.55	2928.68	456.10
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	37.75	453.00	37.75
Basis ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	198.51	179.60	190.61	205.08	209.41	436.43	493.85	467.74	447.28	189.58	177.29	186.30	3381.68	493.85

Charges
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category

Corresponding Sources for Charges
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	160.76	141.85	152.86	167.33	171.66	398.68	456.10	429.99	409.53	151.83	139.54	148.55	2928.68	456.10
AboveCustomerBaseCosts	160.76	141.85	152.86	167.33	171.66	398.68	456.10	429.99	409.53	151.83	139.54	148.55	2928.68	456.10
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	3601.12	3185.65	3463.02	3768.77	3888.02	3237.81	3705.90	3486.54	3318.34	3386.97	3113.33	3312.65	41468.11	3888.02
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
EnergyCharges SUM RealTimePriceCosts
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEI-SELL
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYSURPLUSSOLD:FACILITY
Selected	Yes
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	-3.8	-3.3	-3.4	-3.6	-3.8	-3.4	-4.0	-3.8	-3.7	-4.0	-3.6	-3.7	-44.1	-3.3
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Basis ($)	-3.8	-3.3	-3.4	-3.6	-3.8	-3.4	-4.0	-3.8	-3.7	-4.0	-3.6	-3.7	-44.1	-3.3
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	-3.8	-3.3	-3.4	-3.6	-3.8	-3.4	-4.0	-3.8	-3.7	-4.0	-3.6	-3.7	-44.1	-3.3
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	-3.8	-3.3	-3.4	-3.6	-3.8	-3.4	-4.0	-3.8	-3.7	-4.0	-3.6	-3.7	-44.1	-3.3

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
GENERATEDELECTRICSOLD ($)	-3.8	-3.3	-3.4	-3.6	-3.8	-3.4	-4.0	-3.8	-3.7	-4.0	-3.6	-3.7	-44.1	-3.3	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	189.62	164.35	171.66	180.64	190.00	171.38	197.58	190.31	184.89	198.97	182.03	184.01	2205.43	198.97

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	189.62	164.35	171.66	180.64	190.00	171.38	197.58	190.31	184.89	198.97	182.03	184.01	2205.43	198.97
TotalDemand	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
PeakEnergy	189.62	164.35	171.66	180.64	190.00	171.38	197.58	190.31	184.89	198.97	182.03	184.01	2205.43	198.97
PeakDemand	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	189.62	164.35	171.66	180.64	190.00	171.38	197.58	190.31	184.89	198.97	182.03	184.01	2205.43	198.97
PeakAndShoulderDemand	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
PeakAndMidPeakEnergy	189.62	164.35	171.66	180.64	190.00	171.38	197.58	190.31	184.89	198.97	182.03	184.01	2205.43	198.97
PeakAndMidPeakDemand	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	189.62	164.35	171.66	180.64	190.00	171.38	197.58	190.31	184.89	198.97	182.03	184.01	2205.43	198.97
PeakAndOffPeakDemand	0.9711	0.9683	0.9570	0.9627	0.9683	0.9866	0.9951	1.01	1.01	1.00	1.01	0.9739	11.81	1.01
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
GENERATEDELECTRICSOLD FROM TotalEnergy
EnergyCharges SUM GENERATEDELECTRICSOLD
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Tariff Report
For: EXAMPLEI-NETMETER
Timestamp: 2019-06-19 07:53:09
General
	Parameter
Meter	ELECTRICITYNET:FACILITY
Selected	No
Group	(none)
Qualified	Yes
Disqualifier	n/a
Computation	automatic
Units	kWh

Categories
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
EnergyCharges ($)	221.75	196.38	213.94	233.23	240.37	199.32	228.04	214.26	203.67	207.22	190.53	203.36	2552.07	240.37
DemandCharges ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ServiceCharges ($)	30.00	30.00	30.00	30.00	30.00	30.00	30.00	30.00	30.00	30.00	30.00	30.00	360.00	30.00
Basis ($)	251.75	226.38	243.94	263.23	270.37	229.32	258.04	244.26	233.67	237.22	220.53	233.36	2912.07	270.37
Adjustment ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Surcharge ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Subtotal ($)	251.75	226.38	243.94	263.23	270.37	229.32	258.04	244.26	233.67	237.22	220.53	233.36	2912.07	270.37
Taxes ($)	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
Total ($)	251.75	226.38	243.94	263.23	270.37	229.32	258.04	244.26	233.67	237.22	220.53	233.36	2912.07	270.37

Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max	Category
NETMETEREDCHARGE ($)	221.75	196.38	213.94	233.23	240.37	199.32	228.04	214.26	203.67	207.22	190.53	203.36	2552.07	240.37	EnergyCharges

Corresponding Sources for Charges
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3411.50	3021.29	3291.36	3588.13	3698.02	3066.43	3508.32	3296.23	3133.45	3188.00	2931.31	3128.63	39262.68	3698.02

Ratchets
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Qualifies
Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max

Native Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
TotalEnergy	3411.50	3021.29	3291.36	3588.13	3698.02	3066.43	3508.32	3296.23	3133.45	3188.00	2931.31	3128.63	39262.68	3698.02
TotalDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakEnergy	3411.50	3021.29	3291.36	3588.13	3698.02	3066.43	3508.32	3296.23	3133.45	3188.00	2931.31	3128.63	39262.68	3698.02
PeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
OffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
MidPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsOffPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
OffPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsMidPeak	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
MidPeakExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakExceedsShoulder	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderExceedsPeak	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsWinter	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsNotWinter	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsSpring	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSpring	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsSummer	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotSummer	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
IsAutumn	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
IsNotAutumn	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	1.00	12.00	1.00
PeakAndShoulderEnergy	3411.50	3021.29	3291.36	3588.13	3698.02	3066.43	3508.32	3296.23	3133.45	3188.00	2931.31	3128.63	39262.68	3698.02
PeakAndShoulderDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
PeakAndMidPeakEnergy	3411.50	3021.29	3291.36	3588.13	3698.02	3066.43	3508.32	3296.23	3133.45	3188.00	2931.31	3128.63	39262.68	3698.02
PeakAndMidPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
ShoulderAndOffPeakEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
ShoulderAndOffPeakDemand	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
PeakAndOffPeakEnergy	3411.50	3021.29	3291.36	3588.13	3698.02	3066.43	3508.32	3296.23	3133.45	3188.00	2931.31	3128.63	39262.68	3698.02
PeakAndOffPeakDemand	16.81	18.16	18.83	18.48	17.95	17.58	17.13	17.10	17.15	16.25	16.30	16.45	208.19	18.83
RealTimePriceCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseCosts	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
AboveCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
BelowCustomerBaseEnergy	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Other Variables
	Jan	Feb	Mar	Apr	May	Jun	Jul	Aug	Sep	Oct	Nov	Dec	Sum	Max
NotIncluded	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00

Computation - Automatic
NETMETEREDCHARGE FROM TotalEnergy
EnergyCharges SUM NETMETEREDCHARGE
Basis SUM EnergyCharges DemandCharges ServiceCharges
Subtotal SUM Basis Adjustment Surcharge
Total SUM Subtotal Taxes

Table of Contents
Report: Life-Cycle Cost Report
For: Entire Facility
Timestamp: 2019-06-19 07:53:09
Life-Cycle Cost Parameters
	Value
Name	TYPICALLCC
Discounting Convention	EndOfYear
Inflation Approach	ConstantDollar
Real Discount Rate	0.0300
Nominal Discount Rate	-- N/A --
Inflation	-- N/A --
Base Date	January 2012
Service Date	January 2014
Length of Study Period in Years	22
Tax rate	0.0000
Depreciation Method	None

Use Price Escalation
	MIDWEST COMMERCIAL-ELECTRICITY	MIDWEST COMMERCIAL-ELECTRICITY	MIDWEST COMMERCIAL-NATURAL GAS
Resource	ElectricityPurchased	ElectricitySurplusSold	Gas
Start Date	January 2012	January 2012	January 2012
1	1.007200	1.007200	0.995000
2	1.014800	1.014800	0.971100
3	1.031500	1.031500	0.977400
4	1.049300	1.049300	0.984900
5	1.050500	1.050500	0.989900
6	1.045100	1.045100	1.000000
7	1.042900	1.042900	1.011300
8	1.041000	1.041000	1.028900
9	1.040600	1.040600	1.061600
10	1.044400	1.044400	1.103100
11	1.050500	1.050500	1.132100
12	1.053500	1.053500	1.148400
13	1.052400	1.052400	1.162300
14	1.047800	1.047800	1.178600
15	1.042900	1.042900	1.192500
16	1.039100	1.039100	1.202500
17	1.037200	1.037200	1.213800
18	1.036000	1.036000	1.228900
19	1.034100	1.034100	1.245300
20	1.031900	1.031900	1.264200
21	1.028800	1.028800	1.281800
22	1.034100	1.034100	1.318200

Use Adjustment
	NOELECTRICUSEADJUSTMENT
	ElectricityPurchased
January 2014	1.000000
January 2015	1.000000
January 2016	1.000000
January 2017	1.000000
January 2018	1.000000
January 2019	1.000000
January 2020	1.000000
January 2021	1.000000
January 2022	1.000000
January 2023	1.000000
January 2024	1.000000
January 2025	1.000000
January 2026	1.000000
January 2027	1.000000
January 2028	1.000000
January 2029	1.000000
January 2030	1.000000
January 2031	1.000000
January 2032	1.000000
January 2033	1.000000

Cash Flow for Recurring and Nonrecurring Costs (Without Escalation)
	ANNUALMAINT	PHASE ONE INVESTMENT	PHASE TWO INVESTMENT	FANREPLACEMENT	PLANTREPLACEMENT	RESIDUALVALUE
	Recurring	Nonrecurring	Nonrecurring	Nonrecurring	Nonrecurring	Nonrecurring
January 2012	0.00	51500.00	0.00	0.00	0.00	0.00
January 2013	0.00	0.00	51500.00	0.00	0.00	0.00
January 2014	7000.00	0.00	0.00	0.00	0.00	0.00
January 2015	7000.00	0.00	0.00	0.00	0.00	0.00
January 2016	7000.00	0.00	0.00	0.00	0.00	0.00
January 2017	7000.00	0.00	0.00	0.00	0.00	0.00
January 2018	7000.00	0.00	0.00	0.00	0.00	0.00
January 2019	7000.00	0.00	0.00	0.00	0.00	0.00
January 2020	7000.00	0.00	0.00	0.00	0.00	0.00
January 2021	7000.00	0.00	0.00	0.00	0.00	0.00
January 2022	7000.00	0.00	0.00	0.00	0.00	0.00
January 2023	7000.00	0.00	0.00	0.00	0.00	0.00
January 2024	7000.00	0.00	0.00	0.00	0.00	0.00
January 2025	7000.00	0.00	0.00	12000.00	0.00	0.00
January 2026	7000.00	0.00	0.00	0.00	0.00	0.00
January 2027	7000.00	0.00	0.00	0.00	0.00	0.00
January 2028	7000.00	0.00	0.00	0.00	60000.00	0.00
January 2029	7000.00	0.00	0.00	0.00	0.00	0.00
January 2030	7000.00	0.00	0.00	0.00	0.00	0.00
January 2031	7000.00	0.00	0.00	0.00	0.00	0.00
January 2032	7000.00	0.00	0.00	0.00	0.00	0.00
January 2033	7000.00	0.00	0.00	0.00	0.00	-20000.0

Energy and Water Cost Cash Flows (Without Escalation)
	Gas	Water	ElectricityPurchased	ElectricitySurplusSold
January 2012	0.00	0.00	0.00	0.00
January 2013	0.00	0.00	0.00	0.00
January 2014	1073.95	1671.53	2251.56	-44.1
January 2015	1073.95	1671.53	2251.56	-44.1
January 2016	1073.95	1671.53	2251.56	-44.1
January 2017	1073.95	1671.53	2251.56	-44.1
January 2018	1073.95	1671.53	2251.56	-44.1
January 2019	1073.95	1671.53	2251.56	-44.1
January 2020	1073.95	1671.53	2251.56	-44.1
January 2021	1073.95	1671.53	2251.56	-44.1
January 2022	1073.95	1671.53	2251.56	-44.1
January 2023	1073.95	1671.53	2251.56	-44.1
January 2024	1073.95	1671.53	2251.56	-44.1
January 2025	1073.95	1671.53	2251.56	-44.1
January 2026	1073.95	1671.53	2251.56	-44.1
January 2027	1073.95	1671.53	2251.56	-44.1
January 2028	1073.95	1671.53	2251.56	-44.1
January 2029	1073.95	1671.53	2251.56	-44.1
January 2030	1073.95	1671.53	2251.56	-44.1
January 2031	1073.95	1671.53	2251.56	-44.1
January 2032	1073.95	1671.53	2251.56	-44.1
January 2033	1073.95	1671.53	2251.56	-44.1

Capital Cash Flow by Category (Without Escalation)
	Construction	Salvage	OtherCapital	Total
January 2012	51500.00	0.00	0.00	51500.00
January 2013	51500.00	0.00	0.00	51500.00
January 2014	0.00	0.00	0.00	0.00
January 2015	0.00	0.00	0.00	0.00
January 2016	0.00	0.00	0.00	0.00
January 2017	0.00	0.00	0.00	0.00
January 2018	0.00	0.00	0.00	0.00
January 2019	0.00	0.00	0.00	0.00
January 2020	0.00	0.00	0.00	0.00
January 2021	0.00	0.00	0.00	0.00
January 2022	0.00	0.00	0.00	0.00
January 2023	0.00	0.00	0.00	0.00
January 2024	0.00	0.00	0.00	0.00
January 2025	0.00	0.00	12000.00	12000.00
January 2026	0.00	0.00	0.00	0.00
January 2027	0.00	0.00	0.00	0.00
January 2028	0.00	0.00	60000.00	60000.00
January 2029	0.00	0.00	0.00	0.00
January 2030	0.00	0.00	0.00	0.00
January 2031	0.00	0.00	0.00	0.00
January 2032	0.00	0.00	0.00	0.00
January 2033	0.00	-20000.0	0.00	-20000.0

Operating Cash Flow by Category (Without Escalation)
	Energy	Water	Maintenance	Repair	Operation	Replacement	MinorOverhaul	MajorOverhaul	OtherOperational	Total
January 2012	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
January 2013	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
January 2014	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2015	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2016	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2017	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2018	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2019	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2020	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2021	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2022	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2023	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2024	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2025	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2026	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2027	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2028	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2029	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2030	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2031	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2032	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93
January 2033	3281.40	1671.53	7000.00	0.00	0.00	0.00	0.00	0.00	0.00	11952.93

Monthly Total Cash Flow (Without Escalation)
	January	February	March	April	May	June	July	August	September	October	November	December
2012	51500.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
2013	51500.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00	0.00
2014	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2015	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2016	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2017	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2018	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2019	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2020	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2021	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2022	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2023	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2024	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2025	19377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2026	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2027	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2028	67377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2029	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2030	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2031	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2032	7377.49	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30
2033	-12622.5	356.69	376.38	375.05	387.14	470.62	511.95	495.80	477.00	377.04	370.45	377.30

Present Value for Recurring, Nonrecurring and Energy Costs (Before Tax)
	Category	Kind	Cost	Present Value	Present Value Factor
ANNUALMAINT	Maintenance	Recurring	7000.00	98164.13	14.0234
PHASE ONE INVESTMENT	Construction	Nonrecurring	51500.00	50000.00	0.9709
PHASE TWO INVESTMENT	Construction	Nonrecurring	51500.00	48543.69	0.9426
FANREPLACEMENT	Other Capital	Nonrecurring	12000.00	7933.41	0.6611
PLANTREPLACEMENT	Other Capital	Nonrecurring	60000.00	36300.99	0.6050
RESIDUALVALUE	Salvage	Nonrecurring	-20000.0	-10437.9	0.5219
Gas	Energy	Energy Cost	1073.95	16841.57	15.6820
Water	Water	Water Cost	1671.53	23440.67	14.0234
ElectricityPurchased	Energy	Energy Cost	2251.56	32908.86	14.6160
ElectricitySurplusSold	Energy	Energy Cost	-44.1	-644.7	14.6160
TOTAL				303050.78

Present Value by Category
	Present Value
Construction	98543.69
Salvage	-10437.9
Other Capital	44234.40
Energy	49105.74
Water	23440.67
Maintenance	98164.13
Repair	0.00
Operation	0.00
Replacement	0.00
Minor Overhaul	0.00
Major Overhaul	0.00
Other Operational	0.00
Total Energy	49105.74
Total Operation	170710.54
Total Capital	132340.24
Grand Total	303050.78

Present Value by Year
	Total Cost	Present Value of Costs
January 2012	51500.00	50000.00
January 2013	51500.00	48543.69
January 2014	11952.93	10980.05
January 2015	11952.93	10702.31
January 2016	11952.93	10397.51
January 2017	11952.93	10093.77
January 2018	11952.93	9805.69
January 2019	11952.93	9531.70
January 2020	11952.93	9280.32
January 2021	11952.93	9049.42
January 2022	11952.93	8818.07
January 2023	11952.93	8578.16
January 2024	11952.93	8336.82
January 2025	23952.93	16032.27
January 2026	11952.93	7865.61
January 2027	11952.93	7637.98
January 2028	71952.93	43721.31
January 2029	11952.93	7212.16
January 2030	11952.93	7009.75
January 2031	11952.93	6814.13
January 2032	11952.93	6622.15
January 2033	-8047.1	-3982.1
TOTAL		303050.78